## PM Frequency List
Asset Class | Asset Class Abbreviations | Frequency | Associated Job Plan Numbers | QTY | X | Unit Price | Total
Air Compressor | ACP | Q,A | UJPH-1042Q, UJPH-1042A | 9 | X
Air Conditioning Unit | ACU | Q,A | UJPH-1285Q, UJPH-1285A | 2 | X
Air Handling Unit | AHU | Q,SA,A | UJPH-1000Q, UJPH-1000SA, UJPH-1000A | 5 | X
Automatic Transfer Switch | ATS | A | UJPH-1171A | 17 | X
Building Automation System | BAS | A | UJPH-1109A | 2 | X
Boiler | BOILER | Q,A | UJPH-1144Q, UJPH-1144A, UJPH-1144AIC | 7 | X
Chiller | CHILLER | M,Q,A | UJPH-1052M, UJPH-1052Q, UJPH-1052A | 2 | X
Condensing Unit | COND | Q,A | UJPH-1063Q, UJPH-1063A | 22 | X
Controller | CONTROLLER | A | UJPH-1002A | 18 | X
Computer Room AC Unit | CRAC | Q,SA,A | UJPH-1013Q, UJPH-1013SA, UJPH-1013A | 2 | X
Cooling Tower | CT | SA,A | UJPH-1005SA, UJPH-1005A | 3 | X
Dust Collection System | DUST | Q | UJPH-5090Q | 1 | X
Electrical Disconnect | EDISC | A | UJPH-1176A-IR | 1 | X
Electrical Panelboard | EPB | A | UJPH-1226A-IR | 162 | X
Energy Recovery Ventilator | ERV | Q,SA,A | UJPH-5012Q, UJPH-5012SA, UJPH-5012A | 5 | X
Electrical Switchboard | ESB | A | UJPH-1227A-IR | 5 | X
Electrical Switchgear | ESG | A | UJPH-1210A-IR | 4 | X
Evaporator | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | 24 | X
Fan - Exhaust | FANE | Q | UJPH-1027Q | 95 | X
Fan Coil Unit | FCU | SA,A | UJPH-1012SA, UJPH-1012A | 68 | X
Filter | FILTER | Q | UJPH-5025Q | 1 | X
Fin Tube Heater | FTH | A | UJPH-1094A | 3 | X
Furnace | FURN | Q,A | UJPH-1112Q, UJPH-1112A | 21 | X
Generator | GENERATOR | A | UJPH-1252A | 9 | X
Heat Pump | HP | Q,A | UJPH-1059Q, UJPH-1059A | 69 | X
Heat Exchanger | HTEX - Tube | A | UJPH-1072A | 2 | X
Heat Exchanger | HTEX - Plate and Frame | A | UGSA-HVAC-HXR-01-01Y | 2 | X
Humidifier | HUMID | A | UJPH-1035A-E | 2 | X
Hot Water Heater - Electric | HWH | A | UJPH-1131A | 17 | X
Hot Water Heater - Gas | HWH | Q,A | UJPH-1133Q, UJPH-1133A | 10 | X
Motor Control Center | MCC | A | UJPH-1282A-IR | 1 | X
Power Supply | POWER | A | UJPH-5026A | 2 | X
Pump | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | 48 | X
Roof Top Unit | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | 14 | X
Tank | TANK | A | UJPH-1073A | 11 | X
Tank - Fuel Exterior | TANK | SA,A | UJPH-1077SA, UJPH-1077A | 3 | X
Unit Heater - Electric | UH | A | UJPH-1234A | 99 | X
Unit Heater - Hydronic | UH | SA,A | UJPH-1135SA, UJPH-1135A | 18 | X
Unit Heater - Gas | UH | SA,A | UJPH-1233SA, UJPH-1233A | 12 | X
Unit Heater - Infrared | UH | A | UJPH-1140A | 3 | X
Uninteruptible Power Supply | UPS | SA,A | UJPH-2086SA, UJPH-2086A | 1 | X
Vacuum | VAC | A | UGSA-HVAC-PMP-02-01Y | 1 | X
Variable Air Volume Box | VAV | A | UJPH-1038A | 47 | X
Variable Frequency Drive | VFD | A | UJPH-1036A | 11 | X
Transformer - Dry | XFMR | A | UJPH-1093A-D | 36 | X
D=Daily, W=Weekly, M=Monthly, Q=Quarterly, S=Semi-Annual, A=Annual, B=Biennial, T=Triennial, O=Other
Planned Maintenane Total Cost

## Asset List
Barcode | Asset Class | PM Frequency | EGS Job Plan Number | Original Lvl 3 | Original Lvl 4 | NEW / ADJUSTED LVL 3 | NEW / ADJUSTED LVL 4 | Bldg | FloorLevel | Room | Notes | Serial? | Manufacture | Model? | Voltage | numBelts | Amps | HorsePower | KVA | KW | Phase | RPM | BTU | MotorFrame | CollectedBy | LastInventory | Site | Asset Num Sort | Comments
00000263 | ACP | Q,A | UJPH-1042Q, UJPH-1042A | D3040 : Distribution Systems | D304099 : OTHER | D3060 : CONTROLS AND INSTRUMENTATION | D306004 : AIR COMPRESSOR | Alpha Ridge Apparatus Storage Building | 1 - First Floor | electrical room | air compressor, 175 max pressure | cbv194619 | Ingersol-Rand |  | 230 | [5 empty] | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000263
00000342 | ACP | Q,A | UJPH-1042Q, UJPH-1042A | D3060 : Controls and Instrumentation | D306004 : AIR COMPRESSOR | D3060 : CONTROLS AND INSTRUMENTATION | D306004 : AIR COMPRESSOR | Alpha Ridge Fire Grounds Building | 1 - First Floor | 112 |  | 5409 h21193001 | mako | mkbam8h2n3206 | 208 |  | 55 | 20 |  | 15 | 3 | 1500 |  |  | Entech | 2016-04-22 |  | SORT-00000342
00000504 | ACP | Q,A | UJPH-1042Q, UJPH-1042A | D3060 : Controls and Instrumentation | D306004 : AIR COMPRESSOR | D3060 : CONTROLS AND INSTRUMENTATION | D306004 : AIR COMPRESSOR | Alpha Ridge Landfill - Shop | 1 - First Floor | garage | md91285v |  | champion | 38061 |  |  |  |  | 10 | [5 empty] | Entech | 2016-05-03 |  | SORT-00000504
00000539 | ACP | Q,A | UJPH-1042Q, UJPH-1042A | D3060 : Controls and Instrumentation | D306004 : AIR COMPRESSOR | D3060 : CONTROLS AND INSTRUMENTATION | D306004 : AIR COMPRESSOR | Alpha Ridge Landfill - Transfer Station Control Building | 1 - First Floor | spinkler |  |  | gast | 6lcf-246s-m616nex |  |  |  |  | 1 |  |  | 1 |  |  | Entech | 2016-05-04 |  | SORT-00000539
00000639 | ACP | Q,A | UJPH-1042Q, UJPH-1042A | D3060 : Controls and Instrumentation | D306004 : AIR COMPRESSOR | D3060 : CONTROLS AND INSTRUMENTATION | D306004 : AIR COMPRESSOR | Western Regional Park - Maintenance Building | Exterior |  |  | d067380 | speedaire | 1wd58 | [6 empty] | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000639
00000720 | ACP | Q,A | UJPH-1042Q, UJPH-1042A | D3060 : Controls and Instrumentation | D306004 : AIR COMPRESSOR | D3060 : CONTROLS AND INSTRUMENTATION | D306004 : AIR COMPRESSOR | Glenwood Community Center | 2 - Second Floor | mechanical |  | 54532t0 | devair | udl-5031-45ms |  |  |  | 1 |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000720
00000824 | ACP | Q,A | UJPH-1042Q, UJPH-1042A | D3060 : Controls and Instrumentation | D306004 : AIR COMPRESSOR | D3060 : CONTROLS AND INSTRUMENTATION | D306004 : AIR COMPRESSOR | Glenwood Fire Station No. 13 | Mezzanine |  | R15 | D097626 | CHAMPION | VR5-8 |  |  |  | 5 |  |  | 3 | 3 |  |  | Entech | 2016-05-11 |  | SORT-00000824
00000904 | ACP | Q,A | UJPH-1042Q, UJPH-1042A | D3060 : Controls and Instrumentation | D306004 : AIR COMPRESSOR | D3060 : CONTROLS AND INSTRUMENTATION | D306004 : AIR COMPRESSOR | Scaggsville Public Safety Complex | 0 - Ground Floor | sprinkler |  | d086854 | champion | vrf-8 | [10 empty] | Entech | 2016-05-17 |  | SORT-00000904
00000919 | ACP | Q,A | UJPH-1042Q, UJPH-1042A | D3060 : Controls and Instrumentation | D306004 : AIR COMPRESSOR | D3060 : CONTROLS AND INSTRUMENTATION | D306004 : AIR COMPRESSOR | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room |  | 062193E-111025 | POWEREX | CD-154C2 | 460 | [5 empty] | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000919
00000975 | ACU | Q,A | UJPH-1285Q, UJPH-1285A | D3030 : Cooling Generating Systems | D303099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - AC UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | Ceiling Mounted |  | 10002172 | stultz | ohso84dahu | [10 empty] | Entech | 2016-05-17 |  | SORT-00000975
00001118 | ACU | Q,A | UJPH-1285Q, UJPH-1285A | D3040 : Distribution Systems | D304008 : CENTRAL STATION | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - AC UNIT | Florence Bain Senior Center | 0 - Ground Floor | telecom closet | ac unit-a | [13 empty] | Entech | 2016-05-19 |  | SORT-00001118
00000681 | AHU | Q,SA,A | UJPH-1000Q, UJPH-1000SA, UJPH-1000A | D3040 : Distribution Systems | D304008 : CENTRAL STATION | D3040 : DISTRIBUTION SYSTEMS | D304008 : CENTRAL STATION | Glenwood Library | 2 - Second Floor | mechanical mezzanine 2 | ahu-2 |  | York | ca0061430.25x070g01hc025s035wh02r1bm2.0007.00ana99s | 460 | [5 empty] | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000681
00000683 | AHU | Q,SA,A | UJPH-1000Q, UJPH-1000SA, UJPH-1000A | D3040 : Distribution Systems | D304008 : CENTRAL STATION | D3040 : DISTRIBUTION SYSTEMS | D304008 : CENTRAL STATION | Glenwood Library | 2 - Second Floor | mechanical mezzanine 2 | ahu-1 |  | York | ca0061427.25x070g01hc025s035wh02r1bm2.0007.00ana99s | 460 | [5 empty] | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000683
00000684 | AHU | Q,SA,A | UJPH-1000Q, UJPH-1000SA, UJPH-1000A | D3040 : Distribution Systems | D304008 : CENTRAL STATION | D3040 : DISTRIBUTION SYSTEMS | D304008 : CENTRAL STATION | Glenwood Library | 2 - Second Floor | mechanical mezzanine 1 | ahu-5 |  | York | ca0061439.25x078g01hc025s035wh02l1bm2.0007.00ana99s | 460 | [5 empty] | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000684
00000687 | AHU | Q,SA,A | UJPH-1000Q, UJPH-1000SA, UJPH-1000A | D3040 : Distribution Systems | D304008 : CENTRAL STATION | D3040 : DISTRIBUTION SYSTEMS | D304008 : CENTRAL STATION | Glenwood Library | 2 - Second Floor | mechanical mezzanine 1 | ahu-4 |  | York | ca0061433.25x073g01hc025s035wh02rbm2.0007.00ana99s | 460 | [5 empty] | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000687
00000690 | AHU | Q,SA,A | UJPH-1000Q, UJPH-1000SA, UJPH-1000A | D3040 : Distribution Systems | D304008 : CENTRAL STATION | D3040 : DISTRIBUTION SYSTEMS | D304008 : CENTRAL STATION | Glenwood Library | 2 - Second Floor | mechanical mezzanine 1 | ahu-3 |  | York | ca0061430.25x048g01hc025s035wh04r1bm1.5007.00ana99s | 460 | [5 empty] | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000690
00000249 | ATS | A | UJPH-1171A | D5010 : Electrical Service and Distribution | D501099 : OTHER | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Alpha Ridge Administration Building | Exterior |  | automatic transfer switch |  | cummings | [11 empty] | Entech | 2016-04-21 |  | SORT-00000249
00000288 | ATS | A | UJPH-1171A | D5010 : Electrical Service and Distribution | D501099 : OTHER | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Alpha Ridge Administration Building | 1 - First Floor | fire alarm annuciator room | transfer switch elpa |  | cummins | [11 empty] | Entech | 2016-04-21 |  | SORT-00000288
00000290 | ATS | A | UJPH-1171A | D5010 : Electrical Service and Distribution | D501099 : OTHER | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Alpha Ridge Administration Building | 1 - First Floor | fire alarm annuciator room | transfer switch emp |  | cummins | [11 empty] | Entech | 2016-04-21 |  | SORT-00000290
00000438 | ATS | A | UJPH-1171A | D5090 : Other Electrical Services | D509002 : AUTOMATIC TRANSFER SWITCH | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Alpha Ridge Training Radio Facility | 1 - First Floor | generator room |  |  | cummins | power command | [10 empty] | Entech | 2016-05-02 |  | SORT-00000438
00000485 | ATS | A | UJPH-1171A | D5090 : Other Electrical Services | D509002 : AUTOMATIC TRANSFER SWITCH | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Alpha Ridge Landfill - Shop | Exterior |  |  | 1238339 RE | emerson | e03atsa30400ngxf |  |  | 400 | [7 empty] | Entech | 2016-05-03 |  | SORT-00000485
00000528 | ATS | A | UJPH-1171A | D5090 : Other Electrical Services | D509002 : AUTOMATIC TRANSFER SWITCH | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Alpha Ridge Landfill - Truck Fill Building | 1 - First Floor |  |  |  | cummins | [11 empty] | Entech | 2016-05-04 |  | SORT-00000528
00000553 | ATS | A | UJPH-1171A | D5090 : Other Electrical Services | D509002 : AUTOMATIC TRANSFER SWITCH | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Alpha Ridge Landfill - Weigh Station | Exterior |  |  |  | cummins | [11 empty] | Entech | 2016-05-04 |  | SORT-00000553
00000609 | ATS | A | UJPH-1171A | D5090 : Other Electrical Services | D509002 : AUTOMATIC TRANSFER SWITCH | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Glenwood Community Center | Exterior |  |  |  | cummins | [11 empty] | Entech | 2016-05-04 |  | SORT-00000609
00000650 | ATS | A | UJPH-1171A | D5090 : Other Electrical Services | D509002 : AUTOMATIC TRANSFER SWITCH | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Western Regional Park - Maintenance Building | 0 - Ground Floor | electrical | gen em |  | Generac | gts-generac transfer switch | [10 empty] | Entech | 2016-05-05 |  | SORT-00000650
00000657 | ATS | A | UJPH-1171A | D5090 : Other Electrical Services | D509002 : AUTOMATIC TRANSFER SWITCH | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Western Regional Park - Maintenance Building | 0 - Ground Floor | electrical | gen mdp |  | Generac | gts-generac transfer switch | [10 empty] | Entech | 2016-05-05 |  | SORT-00000657
00000763 | ATS | A | UJPH-1171A | D5090 : Other Electrical Services | D509002 : AUTOMATIC TRANSFER SWITCH | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Glenwood Community Center | 1 - First Floor | electrical room 155 | ats to panel em |  | cummins | [7 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000763
00000764 | ATS | A | UJPH-1171A | D5090 : Other Electrical Services | D509002 : AUTOMATIC TRANSFER SWITCH | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Glenwood Community Center | 1 - First Floor | electrical room 155 | ats to panel eh |  | cummins | [7 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000764
00000843 | ATS | A | UJPH-1171A | D5090 : Other Electrical Services | D509002 : AUTOMATIC TRANSFER SWITCH | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Glenwood Fire Station No. 13 | 1 - First Floor |  |  |  | Kohler | KOHLER POWER SYSTEMS | [10 empty] | Entech | 2016-05-11 |  | SORT-00000843
00000855 | ATS | A | UJPH-1171A | D5090 : Other Electrical Services | D509002 : AUTOMATIC TRANSFER SWITCH | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Glenwood Fire Station No. 13 | 1 - First Floor | FIRE PUMP ROOM |  | 22828059 | HUBBELL | MTS100 |  |  | 100 |  |  |  | 3 |  |  |  | Entech | 2016-05-11 |  | SORT-00000855
00000872 | ATS | A | UJPH-1171A | D5090 : Other Electrical Services | D509002 : AUTOMATIC TRANSFER SWITCH | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Old West Friendship Firehouse | 2 - Second Floor | ELECTRICAL CLOSET |  |  | ZENITH | [11 empty] | Entech | 2016-05-11 |  | SORT-00000872
00000939 | ATS | A | UJPH-1171A | D5090 : Other Electrical Services | D509002 : AUTOMATIC TRANSFER SWITCH | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 |  | b930500976 | cummins | bn800 | [10 empty] | Entech | 2016-05-17 |  | SORT-00000939
00001124 | ATS | A | UJPH-1171A | D5090 : Other Electrical Services | D509002 : AUTOMATIC TRANSFER SWITCH | D5090 : OTHER ELECTRICAL SERVICES | D509002 : AUTOMATIC TRANSFER SWITCH | Florence Bain Senior Center | 0 - Ground Floor | mechanical |  |  | cummins | powercommand | [10 empty] | Entech | 2016-05-19 |  | SORT-00001124
00000243 | BAS | A | UJPH-1109A | D3060 : Controls and Instrumentation | D306099 : OTHER | D3060 : CONTROLS AND INSTRUMENTATION | D306002 : ELECTRONIC CONTROLS - BAS | Alpha Ridge Pump Building | 1 - First Floor |  | metasys controoler |  | johnson controls | nce25 | [10 empty] | Entech | 2016-04-20 |  | SORT-00000243 | Does not include calibration, patches, updates or upgrades
00000458 | BAS | A | UJPH-1109A | D3060 : Controls and Instrumentation | D306099 : OTHER | D3060 : CONTROLS AND INSTRUMENTATION | D306002 : ELECTRONIC CONTROLS - BAS | Alpha Ridge Simulation Training Building | 2 - Second Floor | 210 mechanical room | metasys |  | johnson controls | ms-nce22560-0 | [10 empty] | Entech | 2016-05-03 |  | SORT-00000458 | Does not include calibration, patches, updates or upgrades
00000913 | BOILER | Q,A | UJPH-1144Q, UJPH-1144A | D3020 : Heat Generating Systems | D302001 : BOILER - GAS / STM | D3020 : HEAT GENERATING SYSTEMS | D302001 : BOILER - GAS / STM | Scaggsville Public Safety Complex | 0 - Ground Floor |  | boiler #1 | 070953618 | RBI | MB2000 | [8 empty] | 16999999 |  | Entech | 2016-05-17 |  | SORT-00000913
00000914 | BOILER | Q,A | UJPH-1144Q, UJPH-1144A | D3020 : Heat Generating Systems | D302001 : BOILER - GAS / STM | D3020 : HEAT GENERATING SYSTEMS | D302001 : BOILER - GAS / STM | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room | boiler #2 | 070953649 | RBI | MB2000 | [10 empty] | Entech | 2016-05-17 |  | SORT-00000914
00000703 | BOILER | Q,A | UJPH-1144Q, UJPH-1144A | D3020 : Heat Generating Systems | D302002 : BOILER - GAS/HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : BOILER - GAS/HW | Glenwood Library | 1 - First Floor | mechanical | md106353h, | fa99-491 p | HB Smith | 19a series -s/w-7 | [8 empty] | 676000 |  | Entech | 2016-05-05 |  | SORT-00000703
00000704 | BOILER | Q,A | UJPH-1144Q, UJPH-1144A | D3020 : Heat Generating Systems | D302002 : BOILER - GAS/HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : BOILER - GAS/HW | Glenwood Library | 1 - First Floor | mechanical | md106354h, | fa99-492 p | HB Smith | 19a series -s/w-7 | [8 empty] | 676000 |  | Entech | 2016-05-05 |  | SORT-00000704
00001049 | BOILER | Q,A | UJPH-1144Q, UJPH-1144A | D3020 : Heat Generating Systems | D302002 : BOILER - GAS/HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : BOILER - GAS/HW | Tubman Center - Grassroots | 0 - Basement | mechanical room | boiler b-1 | f07h00199003 | lochinvar | chn0991 | [8 empty] | 831600 |  | Entech | 2016-05-18 |  | SORT-00001049
00001051 | BOILER | Q,A | UJPH-1144Q, UJPH-1144A | D3020 : Heat Generating Systems | D302002 : BOILER - GAS/HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : BOILER - GAS/HW | Tubman Center - Grassroots | 0 - Basement | mechanical room | boiler b-2 | f07h00199002 | lochinvar | chn0991 | [8 empty] | 831600 |  | Entech | 2016-05-18 |  | SORT-00001051
00001132 | BOILER | Q,A | UJPH-1144Q, UJPH-1144A | D3020 : Heat Generating Systems | D302002 : BOILER - GAS/HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : BOILER - GAS/HW | Florence Bain Senior Center | 0 - Ground Floor | mechanical |  |  | lochinvar | knight xl | [8 empty] | 559800 |  | Entech | 2016-05-19 |  | SORT-00001132
00000909 | CHILLER | M,Q,A | UJPH-1052M, UJPH-1052Q, UJPH-1052A | D3030 : Cooling Generating Systems | D303001 : CHILLER - AIR COOLED | D3030 : COOLING GENERATING SYSTEMS | D303001 : CHILLER - AIR COOLED | Scaggsville Public Safety Complex | Exterior |  |  | STNU141000067 | diakin | AGZ080DHHNN-ER10 | 460 | [9 empty] | Entech | 2016-05-17 |  | SORT-00000909 | Seasonal Monthly
00000910 | CHILLER | M,Q,A | UJPH-1052M, UJPH-1052Q, UJPH-1052A | D3030 : Cooling Generating Systems | D303001 : CHILLER - AIR COOLED | D3030 : COOLING GENERATING SYSTEMS | D303001 : CHILLER - AIR COOLED | Scaggsville Public Safety Complex | Exterior |  | CHILLER #1 | 1430404A93H | durham bush | AC80B | 460 | [9 empty] | Entech | 2016-05-17 |  | SORT-00000910
00000246 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Alpha Ridge Administration Building | Exterior |  |  | 6006311 | mitSUBISHI | mu-a09wa | 115 | [5 empty] | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000246
00000309 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Alpha Ridge Kennel | Exterior |  |  | 2207e05052 | Carrier | 24apa518a0030010 | 208/230 |  |  | 1/12 |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000309
00000336 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Alpha Ridge Fire Grounds Building | Exterior |  | accu5 | S3407E03995 | Carrier | ZI24ACR360A0031010 | 208/230 |  |  | 1/ 4 |  |  | 1 |  |  |  | Entech | 2016-04-22 |  | SORT-00000336
00000337 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Alpha Ridge Fire Grounds Building | Exterior |  | accu2 | S3407E04005 | Carrier | ZI24ACR360A0031010 | 208/230 |  |  | 1/ 4 |  |  | 1 |  |  |  | Entech | 2016-04-22 |  | SORT-00000337
00000338 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Alpha Ridge Fire Grounds Building | Exterior |  | accu1 | 1508G20190 | Carrier | 38ARD012---501-- | 208/230 | [5 empty] | 3 |  |  |  | Entech | 2016-04-22 |  | SORT-00000338
00000442 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Alpha Ridge Simulation Training Building | Exterior |  |  | S4113E08231 | Carrier | ZI24ABB360W0034010 | [6 empty] | 1 |  |  |  | Entech | 2016-05-03 |  | SORT-00000442
00000443 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Alpha Ridge Simulation Training Building | Exterior |  |  | 1508G20191 | Carrier | 38ARD012---501-- | [6 empty] | 3 |  |  |  | Entech | 2016-05-03 |  | SORT-00000443
00000526 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Alpha Ridge Landfill - Shop | Exterior |  |  |  | Carrier |  | 115 | [6 empty] | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000526
00000554 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Alpha Ridge Landfill - Weigh Station | Exterior |  |  | gen001187 | fujitsu | aou30clx1 | [6 empty] | 1 | 1 |  |  | Entech | 2016-05-04 |  | SORT-00000554
00000560 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Alpha Ridge Landfill - Weigh Station | 0 - Ground Floor | hallway |  | dna00516 | fujitsu | asu9r2 | [6 empty] | 1 | 1 |  |  | Entech | 2016-05-04 |  | SORT-00000560
00000593 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Glenwood Library | Exterior |  |  | 1-99-g-7064-27 | emi | scc12da0000aa0a |  |  |  | 0.125 |  |  | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000593
00000611 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Glenwood Community Center | Roof |  |  | 65u00288c | mitsubISHI | puy-a42nha | [6 empty] | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000611
00000637 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Western Regional Park - Maintenance Building | Exterior |  |  | S1509E09348 | bryant | 113rna060-h | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000637
00000833 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Glenwood Fire Station No. 13 | Roof |  |  | 1215463N2F | TRANE | 4TTB4036E1000BA |  |  | 19 |  |  |  | 1 |  |  |  | Entech | 2016-05-11 |  | SORT-00000833
00000834 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Glenwood Fire Station No. 13 | Roof |  | ACCU-2 | 121736KR5F | TRANE | 4TTB4024E1000BA |  |  | 9 |  |  |  | 1 |  |  |  | Entech | 2016-05-11 |  | SORT-00000834
00000835 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Glenwood Fire Station No. 13 | Roof |  | ACCU-3 | 12174DSL2F | TRANE | 4TTB4030E1000BA |  |  | 12 |  |  |  | 1 |  |  |  | Entech | 2016-05-11 |  | SORT-00000835
00000836 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Glenwood Fire Station No. 13 | Roof |  | ACCU -4 | 12174DUW2F | TRANE | 4TTB4030E1000BA |  |  | 12 |  |  |  | 1 |  |  |  | Entech | 2016-05-11 |  | SORT-00000836
00000837 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Glenwood Fire Station No. 13 | Roof |  | ACCU -5 | 121736EN5F | TRANE | 4TTB4024E100BA |  |  | 9 |  |  |  | 1 |  |  |  | Entech | 2016-05-11 |  | SORT-00000837
00000879 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Old West Friendship Firehouse | Exterior |  | #5 | 2092EO3738 | BRYANT | 698ANP060-A |  |  |  | 0.25 |  |  | 1 |  |  |  | Entech | 2016-05-11 |  | SORT-00000879
00000908 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Scaggsville Public Safety Complex | Exterior |  |  | agn002528 | fijitsu | aou24d1 | [6 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000908
00001048 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3030 : Cooling Generating Systems | D303001 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Tubman Center - Grassroots | Exterior |  |  |  | harford duracool | [11 empty] | Entech | 2016-05-18 |  | SORT-00001048
00000912 | COND | Q,A | UJPH-1063Q, UJPH-1063A | D3050 : Terminal and Package Units | D305099 : CONDENSING UNIT | D3030 : COOLING GENERATING SYSTEMS | D303001 : CONDENSING UNIT | Scaggsville Public Safety Complex | Exterior |  |  | A4U07700C | mitsubishi | PUY-A24NHA4 | 208/230 | [9 empty] | Entech | 2016-05-17 |  | SORT-00000912
00000614 | CONTROLLER | A | UJPH-1002A | D2020 : Domestic Water Distribution | D202099 : OTHER | D2020 : DOMESTIC WATER DISTRIBUTION | D202099 : OTHER | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | pump room | pump control panel hydro pump 1 |  | hydronic modules | [11 empty] | Entech | 2016-05-04 |  | SORT-00000614
00000616 | CONTROLLER | A | UJPH-1002A | D2020 : Domestic Water Distribution | D202099 : OTHER | D2020 : DOMESTIC WATER DISTRIBUTION | D202099 : OTHER | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | pump room | pump control panel hydro pump 2 |  | hydronic modules | [11 empty] | Entech | 2016-05-04 |  | SORT-00000616
00000620 | CONTROLLER | A | UJPH-1002A | D2020 : Domestic Water Distribution | D202099 : OTHER | D2020 : DOMESTIC WATER DISTRIBUTION | D202099 : OTHER | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | pump room | pump control panel well pump |  | hydronic modules | [11 empty] | Entech | 2016-05-04 |  | SORT-00000620
00000335 | CONTROLLER | A | UJPH-1002A | D3060 : Controls and Instrumentation | D306099 : OTHER | D3060 : CONTROLS AND INSTRUMENTATION | D306099 : OTHER | Alpha Ridge Fire Grounds Building | 2 - Second Floor | mezzanine | temp control panel rpa14 |  | johnson control | metasys nce25 | [10 empty] | Entech | 2016-04-22 |  | SORT-00000335
00000492 | CONTROLLER | A | UJPH-1002A | D3060 : Controls and Instrumentation | D306099 : OTHER | D3060 : CONTROLS AND INSTRUMENTATION | D306099 : OTHER | Alpha Ridge Landfill - Shop | 1 - First Floor | rain water harvest main control panel mcp-1 | rain water harvest |  | allen bradley | panelview c400 | [10 empty] | Entech | 2016-05-03 |  | SORT-00000492
00000649 | CONTROLLER | A | UJPH-1002A | D3060 : Controls and Instrumentation | D306099 : OTHER | D3060 : CONTROLS AND INSTRUMENTATION | D306099 : OTHER | Western Regional Park - Maintenance Building | 0 - Ground Floor | mechanical | pump controller, sump pump 200v,0.75 hp |  | itt | [11 empty] | Entech | 2016-05-05 |  | SORT-00000649
00000669 | CONTROLLER | A | UJPH-1002A | D3060 : Controls and Instrumentation | D306099 : OTHER | D3060 : CONTROLS AND INSTRUMENTATION | D306099 : OTHER | Glenwood Library | 0 - Ground Floor | hallway | hvac control panel, 24 x 24 |  | johnson controls | [11 empty] | Entech | 2016-05-05 |  | SORT-00000669
00000693 | CONTROLLER | A | UJPH-1002A | D3060 : Controls and Instrumentation | D306099 : OTHER | D3060 : CONTROLS AND INSTRUMENTATION | D306099 : OTHER | Glenwood Library | 1 - First Floor | mechanical | central plant control panel |  | johnson controls | [11 empty] | Entech | 2016-05-05 |  | SORT-00000693
00000728 | CONTROLLER | A | UJPH-1002A | D3060 : Controls and Instrumentation | D306099 : OTHER | D3060 : CONTROLS AND INSTRUMENTATION | D306099 : OTHER | Glenwood Community Center | 2 - Second Floor | mechanical | unit 1144 controller panel assembly |  | johnson controls | paue00001fh0 | [10 empty] | Entech | 2016-05-05 |  | SORT-00000728
00000729 | CONTROLLER | A | UJPH-1002A | D3060 : Controls and Instrumentation | D306099 : OTHER | D3060 : CONTROLS AND INSTRUMENTATION | D306099 : OTHER | Glenwood Community Center | 2 - Second Floor | mechanical | dx-9100-8454 controller panel assembly |  | johnson controls | pada00001ah0 | [10 empty] | Entech | 2016-05-05 |  | SORT-00000729
00000730 | CONTROLLER | A | UJPH-1002A | D3060 : Controls and Instrumentation | D306099 : OTHER | D3060 : CONTROLS AND INSTRUMENTATION | D306099 : OTHER | Glenwood Community Center | 2 - Second Floor | mechanical | nae 5521-0 controller panel assembly |  | johnson controls | pagd00001ac0 | [10 empty] | Entech | 2016-05-05 |  | SORT-00000730
00000731 | CONTROLLER | A | UJPH-1002A | D3060 : Controls and Instrumentation | D306099 : OTHER | D3060 : CONTROLS AND INSTRUMENTATION | D306099 : OTHER | Glenwood Community Center | 2 - Second Floor | mechanical | pump controller |  | ames-messco | [11 empty] | Entech | 2016-05-05 |  | SORT-00000731
00000597 | CONTROLLER | A | UJPH-1002A | D4040 : Other Fire Protection Systems |  | D4020 : STANDPIPE SYSTEMS | D402001 : STANDPIPE EQUIPMENT AND PIPING - CONTROLLER | Glenwood Library | Exterior | fire pump pit | jockey pump controller |  | hubbell | 19456494 | [10 empty] | Entech | 2016-05-04 |  | SORT-00000597
00000598 | CONTROLLER | A | UJPH-1002A | D4040 : Other Fire Protection Systems |  | D4020 : STANDPIPE SYSTEMS | D402001 : STANDPIPE EQUIPMENT AND PIPING - CONTROLLER | Glenwood Library | Exterior | fire pump pit | fire pump controller | a-517409-1-1 | hubbell | lxi1900 |  |  |  | 50 |  |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000598
00000666 | CONTROLLER | A | UJPH-1002A | D4040 : Other Fire Protection Systems |  | D4020 : STANDPIPE SYSTEMS | D402001 : STANDPIPE EQUIPMENT AND PIPING - CONTROLLER | Western Regional Park - Maintenance Pump Building | 0 - Ground Floor |  | fire pump controller |  | firetrol | [11 empty] | Entech | 2016-05-05 |  | SORT-00000666
00000851 | CONTROLLER | A | UJPH-1002A | D5010 : Electrical Service and Distribution | D501099 : OTHER | D4020 : STANDPIPE SYSTEMS | D402001 : STANDPIPE EQUIPMENT AND PIPING - CONTROLLER | Glenwood Fire Station No. 13 | 1 - First Floor | FIRE PUMP ROOM |  | 22828089 | HUBBELL | M15A-1.5-208 |  |  | 8 |  |  |  | 3 |  |  |  | Entech | 2016-05-11 |  | SORT-00000851
00000854 | CONTROLLER | A | UJPH-1002A | D5010 : Electrical Service and Distribution | D501099 : OTHER | D4020 : STANDPIPE SYSTEMS | D402001 : STANDPIPE EQUIPMENT AND PIPING - CONTROLLER | Glenwood Fire Station No. 13P | 1 - First Floor | FIRE PUMP ROOM | FIRE PUMP CONTROLLER | 22828059 | HUBBELL | MP700-25-208C MTS | [6 empty] | 3 |  |  |  | Entech | 2016-05-11 |  | SORT-00000854
00000861 | CONTROLLER | A | UJPH-1002A | D5010 : Electrical Service and Distribution | D501099 : OTHER | D4020 : STANDPIPE SYSTEMS | D402001 : STANDPIPE EQUIPMENT AND PIPING - CONTROLLER | Old West Friendship Firehouse | 1 - First Floor |  | FIRE PUMP CONTROLLER |  | FIRETROL | FTA750-AA20H |  |  | 10000 | 20 | [6 empty] | Entech | 2016-05-11 |  | SORT-00000861
00000906 | CRAC | Q,SA,A | UJPH-1013Q, UJPH-1013SA, UJPH-1013A | D3030 : Cooling Generating Systems | D303002 : CRAC UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : CRAC UNIT | Scaggsville Public Safety Complex | Exterior |  | system 2 | 10002174 | stultz | ohs-042-rcu-o | [6 empty] | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000906
00000907 | CRAC | Q,SA,A | UJPH-1013Q, UJPH-1013SA, UJPH-1013A | D3030 : Cooling Generating Systems | D303002 : CRAC UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : CRAC UNIT | Scaggsville Public Safety Complex | Exterior |  | sys 1 | 10002173 | stultz | ohs-042-rcu-o | [6 empty] | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000907
00000592 | CT | SA,A | UJPH-1005SA, UJPH-1005A | D3030 : Cooling Generating Systems | D303001 : COOLING TOWER - GALVANIZED | D3030 : COOLING GENERATING SYSTEMS | D303001 : COOLING TOWER - GALVANIZED | Glenwood Library | Exterior |  |  | rlhm2040aa | York | ycal0080sc46xaasdtxxtxblxxxx44xx1xxxxxxxxaxxxxxxxxxxxxxe | 460 | [5 empty] | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000592
00001047 | CT | SA,A | UJPH-1005SA, UJPH-1005A | D3030 : Cooling Generating Systems | D303001 : COOLING TOWER - GALVANIZED | D3030 : COOLING GENERATING SYSTEMS | D303001 : COOLING TOWER - GALVANIZED | Tubman Center - Grassroots | Exterior |  |  | u070472201 | baltimore air coil | vt0-057 | [10 empty] | Entech | 2016-05-18 |  | SORT-00001047
00001127 | CT | SA,A | UJPH-1005SA, UJPH-1005A | D3030 : Cooling Generating Systems | D303001 : COOLING TOWER - GALVANIZED | D3030 : COOLING GENERATING SYSTEMS | D303001 : COOLING TOWER - GALVANIZED | Florence Bain Senior Center | 0 - Ground Floor | mechanical |  | u135455302-01-01 | baltimore air coil | vxt-70c | [10 empty] | Entech | 2016-05-19 |  | SORT-00001127
00001147 | DUST | Q | UJPH-5090Q | D3090 : Other HVAC Systems and Equipment |  | D3090 : OTHER HVAC SYSTEMS AND EQUIPMENT | D309099 : OTHER SPECIAL MECHANICAL SYSTEMS - DUST COLLECTION | Florence Bain Senior Center | 0 - Ground Floor | wood shop closet | dust collector | [13 empty] | Entech | 2016-05-19 |  | SORT-00001147
00000665 | EDISC | A | UJPH-1176A-IR | D4040 : Other Fire Protection Systems |  | D5020 : LIGHTING AND BRANCH WIRING | D502001 : BRANCH WIRING - DISCONNECT | Western Regional Park - Maintenance Pump Building | 0 - Ground Floor |  | fire disconnect | 498643-01re | firetrol | fta750-ad25h |  |  |  | 25 |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000665 | Subcontracted
00000234 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Maze / Storage Building | 1 - First Floor |  | 18 ckt, panel rpb | aqf312abx | General Electric | axb7 | 120/208 |  | 125 |  |  |  | 3 |  |  |  | Entech | 2016-04-20 |  | SORT-00000234
00000237 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Pump Building | 1 - First Floor |  | 18 ckt, panel rpc | aqf3121abx | General Electric | axb7 | 120/208 |  | 125 |  |  |  | 3 |  |  |  | Entech | 2016-04-20 |  | SORT-00000237
00000238 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Pump Building | 1 - First Floor |  | 30 ckt, panel lpc | aef3301bbx | General Electric | axb7 | 277/480 |  | 125 |  |  |  | 3 |  |  |  | Entech | 2016-04-20 |  | SORT-00000238
00000261 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Apparatus Storage Building | 1 - First Floor | electrical room | panel b |  | General Electric | aqf142cbx | 120/240 |  | 400 |  |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000261
00000262 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Apparatus Storage Building | 1 - First Floor | electrical room | 42 ckt, subpanel a |  | Square-D | nqod42l225cu | 240 |  | 225 |  |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000262
00000265 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Apparatus Storage Building | 1 - First Floor | main warehouse | 20 ckt, subpanel b |  | Square-D | qoc20u100s | 240 |  | 100 |  |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000265
00000271 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Chemical Exposure Building | 1 - First Floor | bay b | 24 ckt w/ main |  | General Electric | aqf3241abx | 120/208 |  | 125 |  |  |  | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000271
00000285 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 1 - First Floor | fire alarm annuciator room | erpa, 18 ckt |  | Siemens | p1c18bl050cts | 208/120 |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000285
00000287 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 1 - First Floor | fire alarm annuciator room | elpa, 30ckt |  | Siemens | p1e30ml125cts | 480/277 |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000287
00000289 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 1 - First Floor | fire alarm annuciator room | emp, 42 ckt |  | Siemens | p1e42ml250cts | 480/277 |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000289
00000292 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 1 - First Floor | main elecTRICAL ROOM | lp1a, 42 ckt |  | Siemens | p1e42ml400cts | 480/277 |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000292
00000293 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 1 - First Floor | main elecTRICAL ROOM | rp1a, 42 ckt |  | Siemens | p1c42ml250cts | 208/120 |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000293
00000294 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 1 - First Floor | main elecTRICAL ROOM | rp1a, 42 ckt |  | Siemens | p1c42ml250cbs | 208/120 |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000294
00000302 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Hogans Alley Structure 2 | 1 - First Floor |  | panel rpf2 |  | General Electric | aqf3121abx | 208/120 |  | 125 |  |  |  | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000302
00000306 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Hogans Alley Structure 3 | 1 - First Floor | main electrical room | panel rpf1 |  | General Electric | aqf3121abx | 208/120 |  | 125 | [7 empty] | Entech | 2016-04-21 |  | SORT-00000306
00000315 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Kennel | 1 - First Floor | storage | panel rph, 24 ckt |  | General Electric | aqf3242abx | 208/120 |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000315
00000316 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Fire Grounds Building | 1 - First Floor | 101 | rpa,42 ckt |  | General Electric | aqf3424sbx | 120/208 |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-04-22 |  | SORT-00000316
00000317 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Fire Grounds Building | 1 - First Floor | 101 | rpa |  | General Electric | aaqf342mbx | 120/208 |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-04-22 |  | SORT-00000317
00000318 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Fire Grounds Building | 1 - First Floor | 101 | rpc |  | General Electric | aqu3302rcx | 120/208 |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-04-22 |  | SORT-00000318
00000341 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Fire Grounds Building | 1 - First Floor | 112 | rps2,30 ckt |  | General Electric | aqf3301mbx | 120/208 |  | 125 |  |  |  | 3 |  |  |  | Entech | 2016-04-22 |  | SORT-00000341
00000371 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 1 - First Floor | server / it | rpcr, 30 ckt |  | Siemens | p1c30ml250cts |  |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000371
00000373 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 1 - First Floor | janitor | rp1b |  | Siemens | p1c42ml250cts |  |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000373
00000374 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 1 - First Floor | janitor | rp1b |  | Siemens | p1c42ml250cbs |  |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000374
00000384 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 1 - First Floor | electrical ROOM | rp1c, 42 ckt |  | Siemens | p1c42ml400cts | 120/208 |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000384
00000385 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 1 - First Floor | electrical ROOM | rp1c, 42 ckt |  | Siemens | p1c42ml400cbs | 120/208 |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000385
00000386 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 1 - First Floor | electrical ROOM | rp1c, 42 ckt |  | Siemens | p1c42ml400cts | 120/208 |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000386
00000387 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 1 - First Floor | electrical ROOM | lp1b, 42 ckt |  | Siemens | p1e42ml400cts | 277/480 |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000387
00000391 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 1 - First Floor | electrical closet | elpb, 18 ckt |  | Siemens | p1e18ml125cts |  |  | 125 |  |  |  | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000391
00000417 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 2 - Second Floor | electrical ROOM | rp2, 42 ckt |  | Siemens | p1c42ml250cts |  |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000417
00000418 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 2 - Second Floor | electrical ROOM | rp2, 42 ckt |  | Siemens | p1c42ml250cbs |  |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000418
00000419 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Administration Building | 2 - Second Floor | electrical ROOM | rp2, 42 ckt |  | Siemens | p1e42ml250cts |  |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000419
00000428 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Police Pistol Range | 1 - First Floor |  |  |  | eaton | eaton | 120/208/240 |  | 125 |  |  |  | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000428
00000429 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Police Pistol Range | 1 - First Floor |  |  |  | eaton | eaton | 120/208/240 |  | 125 |  |  |  | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000429
00000434 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Training Radio Facility | 1 - First Floor |  | pp-2 |  | Cutler-Hammer |  | 120/240 |  | 200 |  |  |  | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000434
00000435 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Training Radio Facility | 1 - First Floor |  | pp-1 |  | Cutler-Hammer | b4242dfn | 120/240 |  | 400 |  |  |  | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000435
00000446 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Simulation Training Building | 1 - First Floor | 119 electrical room | rpe, 42 ckt |  | General Electric | aqf3426mbx axt1b7 |  |  | 600 |  |  |  | 3 |  |  |  | Entech | 2016-05-03 |  | SORT-00000446
00000447 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Simulation Training Building | 1 - First Floor | 119 electrical room | rpe, 42 ckt |  | General Electric | aqf3426mtx axt1b7 |  |  | 600 |  |  |  | 3 |  |  |  | Entech | 2016-05-03 |  | SORT-00000447
00000448 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Simulation Training Building | 1 - First Floor | 119 electrical room | rpe, 42 ckt |  | General Electric | aqf3426mbx axt1b7 |  |  | 600 |  |  |  | 3 |  |  |  | Entech | 2016-05-03 |  | SORT-00000448
00000460 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Park - Comfort Station | 1 - First Floor | mechanical | pnl lb |  | General Electric | aqu3422rcx |  |  |  | 225 |  |  | 3 |  |  |  | Entech | 2016-05-03 |  | SORT-00000460
00000469 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Pump Bldg | 1 - First Floor |  | panel e |  | Square-D | 44-69411-2b |  |  |  | 100 |  |  |  | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000469
00000470 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Pump Bldg | 1 - First Floor |  | panel f |  | Square-D | 44-69411-2a |  |  |  | 50 |  |  |  | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000470
00000480 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Trailer | 1 - First Floor |  | 10 ckt, panel a |  | Siemens | ab1020b1100g |  |  |  | 100 |  |  |  | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000480
00000481 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Trailer | 1 - First Floor |  | 10 ckt, panel b |  | Siemens | ab1020b1100g |  |  |  | 100 |  |  |  | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000481
00000486 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Shop | Exterior |  |  |  | Square-D | nf600sfbh |  |  | 600 |  |  |  |  | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000486
00000493 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Shop | 1 - First Floor | rain water harvest main control panel mcp-1 | panelboard rhp |  | eaton | [8 empty] | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000493
00000496 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Shop | 1 - First Floor | electrical room | panel c |  | Square-D | 44-69411-2b |  |  | 150 |  |  |  |  | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000496
00000497 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Shop | 1 - First Floor | electrical room | panel d |  | Square-D | 44-69411-2a |  |  | 100 |  |  |  |  | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000497
00000499 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Shop | 1 - First Floor | electrical room | panel d-1 |  | Square-D | nqod-30435-1m |  |  | 100 |  |  |  |  | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000499
00000507 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Shop |  |  | panel d4 |  | Siemens | s1c30ml125ats |  |  |  | 125 |  |  |  | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000507
00000519 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Shed | 0 - Ground Floor |  | panel d3 |  | Square-D | nq430l1c | [7 empty] | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000519
00000520 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Storage Building 1 | 0 - Ground Floor |  | panel d2 |  | Square-D | qoc30us | [10 empty] | Entech | 2016-05-03 |  | SORT-00000520
00000521 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Storage Building 2 | 0 - Ground Floor |  |  |  | Square-D | qo8-16100d |  |  | 100 |  |  |  |  | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000521
00000523 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Salt Barn | Exterior |  |  |  | eaton |  |  |  | 125 |  |  |  |  | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000523
00000529 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Truck Fill Building | 1 - First Floor |  | panel pp |  | Square-D | 2586323-h0 | 480 |  | 225 |  |  |  |  | 3 |  |  | Entech | 2016-05-04 |  | SORT-00000529
00000531 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Truck Fill Building | 1 - First Floor |  | panel lpa |  | Square-D | 2586323-10 |  |  | 100 |  |  |  |  | 3 |  |  | Entech | 2016-05-04 |  | SORT-00000531
00000540 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Transfer Station Control Building | 1 - First Floor | electrical room | panel lpc |  | Square-D | 12159449750020001 |  |  | 100 | [7 empty] | Entech | 2016-05-04 |  | SORT-00000540
00000541 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Transfer Station Control Building | 1 - First Floor | electrical room | panel dpc |  | Square-D | 12159449750010001 |  |  | 200 |  |  |  |  | 3 |  |  | Entech | 2016-05-04 |  | SORT-00000541
00000542 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Transfer Station Control Building | 1 - First Floor | electrical room | panel mpc |  | Square-D | 12159449750030001 |  |  | 100 |  |  |  |  | 3 |  |  | Entech | 2016-05-04 |  | SORT-00000542
00000543 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Transfer Station Control Building | 1 - First Floor | electrical room | panel rpc |  | Square-D | 12159449750050001 |  |  | 200 |  |  |  |  | 3 |  |  | Entech | 2016-05-04 |  | SORT-00000543
00000564 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Weigh Station | 0 - Ground Floor | electrical room | panel b |  | Square-D | 44-69411-2a |  |  | 50 |  |  |  |  | 3 |  |  | Entech | 2016-05-04 |  | SORT-00000564
00000566 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Alpha Ridge Landfill - Weigh Station | 0 - Ground Floor | electrical room | panel a |  | Square-D | 44-69411-2b |  |  | 100 |  |  |  |  | 3 |  |  | Entech | 2016-05-04 |  | SORT-00000566
00000574 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Western Regional Park - Concession | 0 - Ground Floor | 108 electrical | panel mdp |  | Square-D | 1220834112001001 |  |  | 800 |  |  |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000574
00000576 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Western Regional Park - Concession | 0 - Ground Floor | 108 electrical | panel l sec 1 |  | Square-D | 1220834112007001 |  |  | 175 |  |  |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000576
00000577 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Western Regional Park - Concession | 0 - Ground Floor | 108 electrical | panel L sec 2 |  | Square-D | 12208341120240001 |  |  | 175 |  |  |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000577
00000578 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Western Regional Park - Concession | 0 - Ground Floor | 108 electrical | panel h |  | Square-D | 12208341120040001 |  |  | 100 |  |  |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000578
00000579 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Western Regional Park - Concession | 0 - Ground Floor | 108 electrical | 150a mcb, field 1 |  | Square-D | 12208341120190001 |  |  | 150 |  |  |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000579
00000580 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Western Regional Park - Concession | 0 - Ground Floor | 108 electrical | mcb 225, field 4 |  | Square-D | 12208341120160001 |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000580
00000581 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Western Regional Park - Concession | 0 - Ground Floor | 108 electrical | 225a mcb, field 5 |  | Square-D | 12208341120160001 |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000581
00000594 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Library | Exterior | fire pump pit | 16 ckt |  | General Electric | tlm16dc | 120/240 | [9 empty] | Entech | 2016-05-04 |  | SORT-00000594
00000595 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Library | Exterior | fire pump pit |  |  | General Electric | aeu3182rcx |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000595
00000621 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | electrical ROOM | 42 ckt |  | eaton | prl3a |  |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000621
00000628 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Western Regional Park - Comfort Station 2 | 0 - Ground Floor |  | panel la, 42 ckt |  | eaton | prl1a |  |  | 100 |  |  |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000628
00000652 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Western Regional Park - Maintenance Building | 0 - Ground Floor | electrical | panel em |  | General Electric | aqf3301cbx |  |  | 125 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000652
00000654 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Western Regional Park - Maintenance Building | 0 - Ground Floor | electrical | panel pl-sec2 |  | General Electric | aqf3422mtx |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000654
00000655 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Western Regional Park - Maintenance Building | 0 - Ground Floor | electrical | panel pl-sec1 |  | General Electric | aqf3422mbx |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000655
00000656 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Western Regional Park - Maintenance Building | 0 - Ground Floor | electrical | panel mdp |  | General Electric | aqf3424jbx |  |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000656
00000662 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Western Regional Park - Maintenance Pump Building | 0 - Ground Floor |  | sub panel pr |  | General Electric | aqf1301mbx |  |  | 125 |  |  |  | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000662
00000670 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Library | 0 - Ground Floor | childrens area | 42 ckt |  | Square-D | nqod442l225cu |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000670
00000671 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Library | 0 - Ground Floor | 129 storage | 30 ckt, c-2 |  | Square-D | nqod430l225cu |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000671
00000672 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Library | 0 - Ground Floor | 129 storage | 30 ckt, c-1 |  | Square-D | nqod430l225cu |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000672
00000677 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Library | 2 - Second Floor | mechanical mezzanine 2 | panel m, 30 ckt |  | Square-D | 12120774650180001 |  |  | 100 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000677
00000694 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Library | 1 - First Floor | mechanical | 30 ckt, panel e-2 |  | Square-D | nqod430l225cu |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000694
00000695 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Library | 1 - First Floor | mechanical | 30 ckt, panel e-1 |  | Square-D | nqod430l225cu |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000695
00000696 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Library | 1 - First Floor | mechanical | panel p |  | Square-D | 12120774650400001 |  |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000696
00000697 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Library | 1 - First Floor | mechanical | panel p1 |  | Square-D | 12120774650170001 |  |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000697
00000707 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Library | 1 - First Floor | electrical | panel b2, 42 ckt |  | Square-D | nqod442l225cu |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000707
00000708 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Library | 1 - First Floor | electrical | panel b1, 42 ckt |  | Square-D | nqod442l225cu |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000708
00000709 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Library | 1 - First Floor | electrical | panel a |  | Square-D | 12-12077465-022 |  |  | 500 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000709
00000711 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Library | 1 - First Floor | electrical | panel mdp |  | Square-D | 12-12077465-021 |  |  | 800 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000711
00000721 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 2 - Second Floor | mechanical | panel p, 30 ckt |  | eaton | prl2a |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000721
00000748 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical c | panel cl sec 1 |  | eaton | prl1a |  |  | 200 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000748
00000749 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical c | panel cl sec 2 |  | eaton | prl1a |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000749
00000750 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical c | panel ch, 42 ckt |  | eaton | prl2a |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000750
00000755 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | gym storage | panel ml sec1, 42ckt |  | eaton | prl1a |  |  | 150 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000755
00000756 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | gym storage | panel ml sec2, 42ckt |  | eaton | prl1a |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000756
00000757 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | gym storage | panel mh, 42ckt |  | eaton | prl2a |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000757
00000759 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical room 155 | panel e |  | eaton | prl1a |  |  | 50 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000759
00000760 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical room 155 | panel eh |  | eaton | prl3a |  |  | 100 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000760
00000761 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical room 155 | panel el |  | eaton | prl3a |  |  | 50 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000761
00000762 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical room 155 | panel em |  | eaton | [7 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000762
00000765 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical room 155 | mdp |  | eaton | prl4b |  |  | 800 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000765
00000768 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical room 155 | mp |  | eaton | prl4b |  |  | 800 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000768
00000795 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical closet 180 | panel kl sec 1 |  | eaton | prl1a |  |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000795
00000796 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical closet 180 | panel kl sec 2 |  | eaton | prl1a |  |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000796
00000797 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical closet 180 | panel kh, 42ckt |  | eaton | prl2a |  |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000797
00000803 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical 182 | panel bl sec 1 |  | eaton | prl1a |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000803
00000804 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical 182 | panel bl sec 2 |  | eaton | prl1a |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000804
00000805 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Community Center | 1 - First Floor | electrical 182 | panel bh |  | eaton | prl2a |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000805
00000825 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Fire Station No. 13 | Mezzanine |  | M 42 CIRCUITS |  | General Electric | axb5 |  |  | 225 | [7 empty] | Entech | 2016-05-11 |  | SORT-00000825
00000839 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Fire Station No. 13 | 1 - First Floor |  | A 30 CIRCUITS |  | General Electric |  |  |  | 225 | [7 empty] | Entech | 2016-05-11 |  | SORT-00000839
00000840 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Fire Station No. 13 | 1 - First Floor |  | A 30 CIRCUITS |  | General Electric | A SERIES 2 |  |  | 225 | [7 empty] | Entech | 2016-05-11 |  | SORT-00000840
00000841 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Fire Station No. 13 | 1 - First Floor |  | DP 4 BREAKERS |  | General Electric | APF6518CDH |  |  | 100 |  |  |  | 3 |  |  |  | Entech | 2016-05-11 |  | SORT-00000841
00000852 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Glenwood Fire Station No. 13 | 1 - First Floor | FIRE PUMP ROOM | A SERIES 2 18 CIRCUITS |  | General Electric | AQU3182RCX |  |  | 225 | [7 empty] | Entech | 2016-05-11 |  | SORT-00000852
00000862 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Old West Friendship Firehouse | 1 - First Floor |  | 20 CIRCUITS |  | SQUARE D | SERIES G1 | [6 empty] | 1 |  |  |  | Entech | 2016-05-11 |  | SORT-00000862
00000866 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Old West Friendship Firehouse | 1 - First Floor | GARAGE | 42 CIRCUITS |  | SQUARE D | [11 empty] | Entech | 2016-05-11 |  | SORT-00000866
00000867 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Old West Friendship Firehouse | 1 - First Floor | GARAGE | 12 CIRCUITS SERIES G1 |  | SQUARE D | [11 empty] | Entech | 2016-05-11 |  | SORT-00000867
00000873 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Old West Friendship Firehouse | 2 - Second Floor | Electrical CLOSET | 42 CIRCUITS |  | EATON | [11 empty] | Entech | 2016-05-11 |  | SORT-00000873
00000929 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | pp2c-ups |  | Square-D | nqod442l225cu |  |  | 225 | [7 empty] | Entech | 2016-05-17 |  | SORT-00000929
00000930 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | panel p2nk |  | Square-D | 1226436850020001 | 120/208 |  | 100 | [7 empty] | Entech | 2016-05-17 |  | SORT-00000930
00000931 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | panel y |  | Square-D | nqod424l100cu | 120/208 |  | 100 | [7 empty] | Entech | 2016-05-17 |  | SORT-00000931
00000932 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | panel f |  | Square-D | nqod430l100cu | 120/208 |  | 100 | [7 empty] | Entech | 2016-05-17 |  | SORT-00000932
00000933 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | panel q |  | Square-D | nqod442l225cu | 120/208 |  | 225 | [7 empty] | Entech | 2016-05-17 |  | SORT-00000933
00000934 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | panel k |  | Square-D | nehb-42441-2cu | 277/480 | [9 empty] | Entech | 2016-05-17 |  | SORT-00000934
00000935 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | panel e |  | Square-D | nqod442m225cu | 120/208 |  | 225 | [7 empty] | Entech | 2016-05-17 |  | SORT-00000935
00000936 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | panel a |  | Square-D | nehb-42441-2cu | 277/480 |  | 225 | [7 empty] | Entech | 2016-05-17 |  | SORT-00000936
00000945 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | panel g |  | General Electric | aqf3361abxaxb4 | 120/208 |  | 125 | [7 empty] | Entech | 2016-05-17 |  | SORT-00000945
00000946 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | panel b |  | General Electric | aqf3301bbxaxb4 | 277/480 |  | 125 |  |  |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000946
00000949 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 1 - First Floor | electrical room | panel m |  | General Electric | aef3301bbx |  |  | 125 |  |  |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000949
00000950 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 1 - First Floor | electrical room | panel r |  | General Electric | aqf3421abx |  |  | 125 |  |  |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000950
00000968 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | duty officers section | panel pc |  | Square-D | nqod442m100cu |  |  | 100 |  |  |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000968
00000969 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | duty officers section | panel p |  | Square-D | nqod |  |  | 100 |  |  |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000969
00000970 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | duty officers section | panel c |  | Square-D |  |  |  | 125 |  |  |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000970
00000971 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | duty officers section | panel j |  | Square-D |  |  |  | 70 |  |  |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000971
00000972 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | it closet | panel |  | General Electric | aqf323241mb |  |  | 125 |  |  |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000972
00000976 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | server room | pp 1 generator |  | Square-D | nqod442l225cu |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000976
00000977 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | server room | pp 2a-ups |  | Square-D | nqod442l225cu |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000977
00000978 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | server room | pp 2b-ups |  | Square-D | nqod442l225cu |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000978
00001012 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | firestation electrical room | panel n |  | Square-D | nqod442l225cu |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001012
00001013 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | firestation electrical room | panel L |  | Square-D | nehb-30435-1cu |  |  | 125 |  |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001013
00001014 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | firestation electrical room | panel h |  | Square-D | nqod442m225cu |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001014
00001015 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | firestation electrical room | panel d |  | Square-D | nehb-42441-2cu |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001015
00001016 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | firestation electrical room | panel h1, cat no p1c30bl09ats |  | siemens |  |  |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001016
00001017 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | firestation electrical room | panel n1, cat no p1c30ml125ats |  | siemens |  |  |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001017
00001024 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Scaggsville Public Safety Complex | 0 - Ground Floor | fire station corridor | panel t |  | Square-D | nqod |  |  | 90 |  |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001024
00001033 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Tubman Center - Grassroots | attic |  | panel rpa |  | siemens | p1c42ml400cbs |  |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001033
00001040 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Tubman Center - Grassroots | 2 - Second Floor | janitor | panel rp2a |  | siemens | p1c42ml250cts |  |  | 250 | [7 empty] | Entech | 2016-05-18 |  | SORT-00001040
00001041 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Tubman Center - Grassroots | 2 - Second Floor | storage | panel rp2b |  | siemens | p1c42ml250ctf |  |  | 250 | [7 empty] | Entech | 2016-05-18 |  | SORT-00001041
00001042 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Tubman Center - Grassroots | 2 - Second Floor | 206 |  |  | Square-D | nq418l1c | 240 |  | 100 |  |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001042
00001044 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Tubman Center - Grassroots | 1 - First Floor | corridor | panel rp1b |  | siemens | p1c42ml250cbf |  |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001044
00001045 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Tubman Center - Grassroots | 1 - First Floor | kitchen | panel k |  | siemens | p1c42ml250cbs |  |  | 250 |  |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001045
00001072 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Tubman Center - Grassroots | 0 - Basement | electrical room | mdp |  | Siemens | p5c75n1120fts |  |  | 1200 |  |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001072
00001073 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Tubman Center - Grassroots | 0 - Basement | electrical room | panel rpb section 1 |  | Siemens | p1c42ml400cts |  |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001073
00001074 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Tubman Center - Grassroots | 0 - Basement | electrical room | panel rpb section 2 |  | Siemens | p1c42ml400cbs |  | 400 |  |  |  | 3 |  |  |  |  | Entech | 2016-05-18 |  | SORT-00001074
00001083 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Tubman Center - Grassroots | 1 - First Floor | 128 | panel rp1a |  | Siemens | p1c42ml250cbs | [6 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001083
00001104 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Florence Bain Senior Center | 0 - Ground Floor | corridor | b sect 1 |  | Westinghouse | wg18585It3 |  |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001104
00001105 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Florence Bain Senior Center | 0 - Ground Floor | corridor | b sect 2 |  | Westinghouse | wg18585It4 |  |  | 400 |  |  |  | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001105
00001106 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Florence Bain Senior Center | 0 - Ground Floor | corridor | panel hp |  | Westinghouse | wg-18585It5 |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001106
00001122 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Florence Bain Senior Center | 0 - Ground Floor | mechanical | panel m |  | Westinghouse | wg185851t6 |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001122
00001123 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Florence Bain Senior Center | 0 - Ground Floor | mechanical | panel a1 |  | Westinghouse | wg-18585It2 |  |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001123
00001125 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Florence Bain Senior Center | 0 - Ground Floor | mechanical | panel p |  | Square-D | nqod442l225cu | 240 |  | 225 |  |  |  | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001125
00001136 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Florence Bain Senior Center | 0 - Ground Floor | corridor-outside of restrooms | panel a |  | Westinghouse | Westinghouse |  |  | 225 |  |  |  |  | 3 |  |  | Entech | 2016-05-19 |  | SORT-00001136
00001146 | EPB | A | UJPH-1226A-IR | D5010 : Electrical Service and Distribution | D501005 : PANEL - BREAKER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501005 : PANEL - BREAKER | Florence Bain Senior Center | 0 - Ground Floor | wood shop | panel s |  | Westinghouse | wg185851t7 |  |  | 150 |  |  |  | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001146
00000605 | ERV | Q,SA,A | UJPH-5012Q, UJPH-5012SA, UJPH-5012A | D3010 : Energy Supply | D301099 : OTHER | D3010 : ENERGY SUPPLY | D301099 : OTHER | Glenwood Community Center | Roof |  | energy recovery unit #2 | 205164-2 | innovent | e-5000-1/sp-4200-hg/hp-1-a | [6 empty] | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000605
00000606 | ERV | Q,SA,A | UJPH-5012Q, UJPH-5012SA, UJPH-5012A | D3010 : Energy Supply | D301099 : OTHER | D3010 : ENERGY SUPPLY | D301099 : OTHER | Glenwood Community Center | Roof |  | energy recovery unit #4 | 205164-4 | innovent | e-5000-1/sp-8200-hg/hp-1-a | [6 empty] | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000606
00000607 | ERV | Q,SA,A | UJPH-5012Q, UJPH-5012SA, UJPH-5012A | D3010 : Energy Supply | D301099 : OTHER | D3010 : ENERGY SUPPLY | D301099 : OTHER | Glenwood Community Center | Roof |  | energy recovery unit #3 | 205164-3 | innovent | e-5000-1/sp-8200-hg/hp-1-a | [6 empty] | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000607
00000610 | ERV | Q,SA,A | UJPH-5012Q, UJPH-5012SA, UJPH-5012A | D3010 : Energy Supply | D301099 : OTHER | D3010 : ENERGY SUPPLY | D301099 : OTHER | Glenwood Community Center | Roof |  | energy recovery unit #1 | 205164-1 | innovent | e-rhxc-1/sp-12005-hg/hp-1-a | [6 empty] | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000610
00001032 | ERV | Q,SA,A | UJPH-5012Q, UJPH-5012SA, UJPH-5012A | D3010 : Energy Supply | D301099 : OTHER | D3010 : ENERGY SUPPLY | D301099 : OTHER | Tubman Center - Grassroots | attic |  | energy recovery unit, 2 5 hp motors | 1078593 | renewaire | he4xin | [6 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001032
00000938 | ESB | A | UJPH-1227A-IR | D5010 : Electrical Service and Distribution | D501003 : SWITCHBOARD | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501003 : SWITCHBOARD | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | switchboard n |  | Square-D | 3745114 V0 | 277/480 |  | 1200 | [7 empty] | Entech | 2016-05-17 |  | SORT-00000938
00000940 | ESB | A | UJPH-1227A-IR | D5010 : Electrical Service and Distribution | D501003 : SWITCHBOARD | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501003 : SWITCHBOARD | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | switchboard e |  | Square-D | 3745114 U0 | 277/480 |  | 1000 |  |  |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000940
00001126 | ESB | A | UJPH-1227A-IR | D5010 : Electrical Service and Distribution | D501003 : SWITCHBOARD | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501003 : SWITCHBOARD | Florence Bain Senior Center | 0 - Ground Floor | mechanical |  |  | Westinghouse | power-line |  |  | 1200 |  |  |  | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001126
00000766 | ESB | A | UJPH-1227A-IR | D5010 : Electrical Service and Distribution | D501099 : OTHER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501003 : SWITCHBOARD | Glenwood Community Center | 1 - First Floor | electrical room 155 | switchboard, sec 1 |  | eaton | power-r-line c |  |  | 1600 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000766
00000767 | ESB | A | UJPH-1227A-IR | D5010 : Electrical Service and Distribution | D501099 : OTHER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501003 : SWITCHBOARD | Glenwood Community Center | 1 - First Floor | electrical room 155 | switchboard, sec 2 |  | eaton | power-r-line c |  |  | 1600 |  |  |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000767
00000296 | ESG | A | UJPH-1210A-IR | D5010 : Electrical Service and Distribution | D501003 : SWITCHGEAR | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501003 : SWITCHGEAR | Alpha Ridge Administration Building | 1 - First Floor | main elecTRICAL ROOM | swbb |  | Siemens | p5c75n1101ets | 208/120 | [5 empty] | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000296
00000299 | ESG | A | UJPH-1210A-IR | D5010 : Electrical Service and Distribution | D501003 : SWITCHGEAR | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501003 : SWITCHGEAR | Alpha Ridge Administration Building | 1 - First Floor | main electrical room | switchboard swba |  | Siemens | 17-37070-a00010-01 | 480/277 |  | 2000 |  |  |  | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000299
00000300 | ESG | A | UJPH-1210A-IR | D5010 : Electrical Service and Distribution | D501003 : SWITCHGEAR | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501003 : SWITCHGEAR | Alpha Ridge Administration Building | 1 - First Floor | main electrical room | switchboard swba |  | Siemens | 17-37070-a00010-02 | 480/277 |  | 2000 |  |  |  | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000300
00000301 | ESG | A | UJPH-1210A-IR | D5010 : Electrical Service and Distribution | D501003 : SWITCHGEAR | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501003 : SWITCHGEAR | Alpha Ridge Administration Building | 1 - First Floor | main electrical room | switchboard swba |  | Siemens | 17-37070-a00010-03 | 480/277 |  | 2000 |  |  |  | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000301
00000270 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Chemical Exposure Building | 1 - First Floor | bay b | evap-1 | 3809a69974 | Carrier | ZIFY4ANF024000AAAA | 208/230 |  |  | 1/4 |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000270
00000329 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Fire Grounds Building | 2 - Second Floor | 101 | upper lobby | 1002586 | mitSUBISHI | msy-ge15na | 208/230 | [5 empty] | 1 |  |  |  | Entech | 2016-04-22 |  | SORT-00000329
00000332 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Fire Grounds Building | 2 - Second Floor |  |  | W080414296 | magic aire | vx-10v dual w cab | 115 | [9 empty] | Entech | 2016-04-22 |  | SORT-00000332
00000363 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Administration Building | 1 - First Floor | elevator machine room |  | 6001241 | mitsubishi | ms-a09wa | 115 | [5 empty] | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000363
00000370 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Administration Building | 1 - First Floor | server / it |  | 65a00157c | mitsubishi | pca-a36ga | [6 empty] | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000370
00000405 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Administration Building | 2 - Second Floor | south stairs |  |  | mitsubishi | [11 empty] | Entech | 2016-05-02 |  | SORT-00000405
00000451 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Simulation Training Building | 2 - Second Floor | mechanical room |  | S2313X29434 | Carrier | ZICNPVP6024ALAAAAA | [10 empty] | Entech | 2016-05-03 |  | SORT-00000451
00000456 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Simulation Training Building | 2 - Second Floor | 210 mechanical room |  | W080414295 | magic aire | vx-10v dual w/ cab | [10 empty] | Entech | 2016-05-03 |  | SORT-00000456
00000506 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Landfill - Shop | 1 - First Floor | parts storage |  | 2893y30592 | Carrier | 42kb009101 | [7 empty] | 1 |  | 9700 | Entech | 2016-05-03 |  | SORT-00000506
00000512 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Landfill - Shop | 2 - Second Floor | supervisor office |  | e003298 | daikin | fxzq18mvju9 | [7 empty] | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000512
00000513 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Landfill - Shop | 2 - Second Floor | open office |  | c001645 | daikin | fxfq36tvju | [7 empty] | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000513
00000514 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Landfill - Shop | 2 - Second Floor | supervisor office |  | e003281 | daikin | fxzq18mvju9 | [7 empty] | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000514
00000515 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Landfill - Shop | 2 - Second Floor | hallway |  | e002167 | daikin | fxfq09mvju9 | [7 empty] | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000515
00000516 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Landfill - Shop | 2 - Second Floor | office |  | e003285 | daikin | fxzq18mvju9 | [7 empty] | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000516
00000517 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Landfill - Shop | 2 - Second Floor | office |  | e003563 | daikin | fxzq12mvju9 | [7 empty] | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000517
00000559 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Landfill - Weigh Station | 0 - Ground Floor | main |  | gea000928 | fijitsu | asu30clx1 | [6 empty] | 1 | 1 |  |  | Entech | 2016-05-04 |  | SORT-00000559
00000645 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Western Regional Park - Maintenance Building | 0 - Ground Floor | mechanical |  | S1908X27070 | bryant | CNRVP6024ATAABAA | [10 empty] | Entech | 2016-05-05 |  | SORT-00000645
00000668 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Glenwood Library | 0 - Ground Floor | telecom room |  | 1-99-D-9906-16 | emi | wsp12d050aa00c |  |  |  | 0.02 |  |  | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000668
00000974 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor |  |  | aga006335 | fijitsu | asu12d1 | [6 empty] | 1 | 1 |  |  | Entech | 2016-05-17 |  | SORT-00000974
00000979 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | server room |  | aga005502 | fijitsu | asu12d1 | [6 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000979
00001043 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Tubman Center - Grassroots | 2 - Second Floor | 206 |  |  | fitjitsu | [11 empty] | Entech | 2016-05-18 |  | SORT-00001043
00001081 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303002 : EVAPORATOR UNIT | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Tubman Center - Grassroots | 0 - Basement | kitchen |  | d07l08271 | heatcraft | lsc065ak0lk | 115 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00001081
00000326 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Fire Grounds Building | 2 - Second Floor |  | cooling coil, gas furnace 1 | S0808X38383 | Carrier | ZICNPVP6024ATAABAA | [10 empty] | Entech | 2016-04-22 |  | SORT-00000326
00000328 | EVAP | SA,A | UJPH-5013SA, UJPH-5013A | D3030 : Cooling Generating Systems | D303099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : EVAPORATOR UNIT | Alpha Ridge Fire Grounds Building | 2 - Second Floor |  | cooling coil, gas furnace 2 | S0908X20704 | Carrier | ZICNPVP6024ATAABAA | [10 empty] | Entech | 2016-04-22 |  | SORT-00000328
00001028 | FANE | Q | UJPH-1027Q | D3020 : Heat Generating Systems | D302099 : HEATING VENTILATION UNIT | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Tubman Center - Grassroots | attic |  | sf-1 |  | captiveaire |  | 208 | [5 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001028
00000253 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Administration Building | Low Roof |  | ef-7 | f06aa81033 | Penn barry | dx11b | 115 |  |  | 1/4 |  |  | 1 | 1074 |  |  | Entech | 2016-04-21 |  | SORT-00000253
00000254 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Administration Building | Low Roof |  | ef-8 |  | Penn barry | dx08b | 115 |  |  | 1/4 |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000254
00000255 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Administration Building | Low Roof |  | ef-6 |  | Penn barry | dx08b | 115 |  |  | 1/4 |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000255
00000259 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Administration Building | Roof |  | ef-1 |  | Penn barry | dx08b | 115 |  |  | 1/4 |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000259
00000260 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Administration Building | Roof |  | ef-5 |  | Penn barry | dx08b | 115 |  |  | 1/4 |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000260
00000274 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Chemical Exposure Building | Roof |  | F-16 | 111522740801 | greenheck | 6b-071-6-x | [10 empty] | Entech | 2016-04-21 |  | SORT-00000274
00000275 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Chemical Exposure Building | Roof |  | F-15 | 111522730801 | greenheck | 6b-101-4-x | [10 empty] | Entech | 2016-04-21 |  | SORT-00000275
00000278 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Administration Building | Roof |  | ef-2 |  | Penn barry | dx08b | 115 |  |  | 1/4 |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000278
00000279 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Administration Building | Roof |  | ef-1 |  | Penn barry | dx08r | 115 | [5 empty] | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000279
00000482 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Landfill - Shop | Exterior |  |  |  | penn industries | [11 empty] | Entech | 2016-05-03 |  | SORT-00000482
00000483 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Landfill - Shop | Exterior |  |  |  | penn industries | [11 empty] | Entech | 2016-05-03 |  | SORT-00000483
00000509 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Landfill - Shop | Roof |  | ef-1 | K15AA81215 | Pennbarry | dx24b | [7 empty] | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000509
00000524 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Landfill - Shop | Exterior |  | f-3 |  | Penn Ventilator |  | 115 | [9 empty] | Entech | 2016-05-03 |  | SORT-00000524
00000525 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Landfill - Shop | Exterior |  | f-2 |  | Penn Ventilator | waq10 | [10 empty] | Entech | 2016-05-03 |  | SORT-00000525
00000527 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Landfill - Shop | Exterior |  | f-1 |  | Penn Ventilator | xr-82 | [10 empty] | Entech | 2016-05-03 |  | SORT-00000527
00000537 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Landfill - Truck Fill Building | Roof |  |  |  | Penn Ventilator | emx90 | [10 empty] | Entech | 2016-05-04 |  | SORT-00000537
00000552 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Landfill - Transfer Station Control Building | Exterior |  |  | 02l14306 | greenheck | cw-070-d6ex-qd | [10 empty] | Entech | 2016-05-04 |  | SORT-00000552
00000556 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Landfill - Weigh Station | Exterior | [15 empty] | Entech | 2016-05-04 |  | SORT-00000556
00000557 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Landfill - Weigh Station | 0 - Ground Floor |  |  |  | Penn industries | 1c8cw | [6 empty] | 1 | 1 |  |  | Entech | 2016-05-04 |  | SORT-00000557
00000590 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Glenwood Library | Roof |  | ef-3 |  | Penn Ventilator | dx13r | [10 empty] | Entech | 2016-05-04 |  | SORT-00000590
00000591 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Glenwood Library | Roof |  | ef-4 |  | Penn Ventilator | dx13r | [10 empty] | Entech | 2016-05-04 |  | SORT-00000591
00000602 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Glenwood Library | Exterior | fire pump pit |  |  | Dayton | ac44a | [6 empty] | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000602
00000603 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Glenwood Library | Roof |  | dx16vsr | b15ax97917 | pennbarry | dx16r | [6 empty] | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000603
00000604 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Glenwood Library | Roof |  | dx16vsr | b15ax97916 | pennbarry | dx16r | [6 empty] | 1 | 1550 |  |  | Entech | 2016-05-04 |  | SORT-00000604
00000612 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Glenwood Community Center | Roof |  |  |  | Penn Ventilator | fx12bhft | [10 empty] | Entech | 2016-05-04 |  | SORT-00000612
00000714 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Glenwood Library | 1 - First Floor | mechanical |  |  | Penn Ventilation | z-15ra | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000714
00000739 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Glenwood Community Center | 2 - Second Floor | mechanical | supply fan ef-5 |  | Penn Ventilator | sx115rc | [10 empty] | Entech | 2016-05-05 |  | SORT-00000739
00000831 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Glenwood Fire Station No. 13 | Mezzanine |  | SF-1 | .3318OS1BSPAO48-75PK | CAPTIVE AIRE | INLINE1L-G10 |  |  |  | 0.33 |  |  | 1 |  |  |  | Entech | 2016-05-11 |  | SORT-00000831
00000853 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Glenwood Fire Station No. 13 | 1 - First Floor | FIRE PUMP ROOM | 160 CFM |  | COOLAIR | CFL15A1151 | [10 empty] | Entech | 2016-05-11 |  | SORT-00000853
00000859 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Glenwood Fire Station No. 13 | 1 - First Floor | MAINTENANCE SHOP | KITCHEN HOOD EF-5 |  | CAPTIVE AIRE | DU50HFA |  |  | 8.1 | 0.5 | [6 empty] | Entech | 2016-05-11 |  | SORT-00000859
00000868 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Old West Friendship Firehouse | 1 - First Floor | GARAGE | AHU MD-214 | 39639 | HASTINGS | 1HVA-600FS |  |  | 5.7 | 1.5 |  |  |  | 1730 |  |  | Entech | 2016-05-11 |  | SORT-00000868
00000882 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | rff-14 | 95a12593 | greenheck | g150bx | [10 empty] | Entech | 2016-05-17 |  | SORT-00000882
00000883 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | rfp-19 | 95a12609 | greenheck | g-60-dge-x | [10 empty] | Entech | 2016-05-17 |  | SORT-00000883
00000884 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | rff-13 | 95a12555 | greenheck | g-80-dgf-x | [10 empty] | Entech | 2016-05-17 |  | SORT-00000884
00000885 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | rff-12 | 95a12653 | greenheck | g-75-dge-x | [10 empty] | Entech | 2016-05-17 |  | SORT-00000885
00000886 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | ref-11 | rrc286208 | acme | pnn245h 4607370d | [6 empty] | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000886
00000887 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | ref-10 | rrc286208 | acme | prn126e | [6 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000887
00000888 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof | [15 empty] | Entech | 2016-05-17 |  | SORT-00000888
00000889 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | ref-18 | rrc286201 | acme | prn171f | [6 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000889
00000890 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | ref-8 | rrc286203 | acme | prn100 | [6 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000890
00000891 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | ref-7 | rrc286201 | acme | prn171f | [6 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000891
00000893 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | ref-5 | rrc286205 | acme | prn163f | [10 empty] | Entech | 2016-05-17 |  | SORT-00000893
00000894 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  |  |  | acme | [11 empty] | Entech | 2016-05-17 |  | SORT-00000894
00000895 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  |  | 93-97493-1-1 | twin city | 122bcv | [10 empty] | Entech | 2016-05-17 |  | SORT-00000895
00000896 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | ref-3 | rrc286203 | acme | prn100 | [10 empty] | Entech | 2016-05-17 |  | SORT-00000896
00000898 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  |  | 9397493-2-1 | twin city | 122bcv | [10 empty] | Entech | 2016-05-17 |  | SORT-00000898
00000899 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | ref-1 | rrc286201 | acme | prn171f | [6 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000899
00000902 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | kef | 12338465 1102 | greenheck | curb-121-s-6 | [10 empty] | Entech | 2016-05-17 |  | SORT-00000902
00000903 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | ef-20 | 12330667 1102 | greenheck | gb-081-4 | [10 empty] | Entech | 2016-05-17 |  | SORT-00000903
00000937 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | ef-15 | rrc286210 | acme | xb245j |  |  |  | 1 | [6 empty] | Entech | 2016-05-17 |  | SORT-00000937
00001068 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Tubman Center - Grassroots | 0 - Basement | mechanical room | ef-3 | [13 empty] | Entech | 2016-05-18 |  | SORT-00001068
00001075 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Tubman Center - Grassroots | 0 - Basement | electrical room | b-1 ef |  | tjernlund | power venter hs4 | 115 | [6 empty] | 1725 |  |  | Entech | 2016-05-18 |  | SORT-00001075
00001076 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Tubman Center - Grassroots | 0 - Basement | electrical room | b-2 ef |  | tjernlund | power venter hs4 | 115 | [6 empty] | 1725 |  |  | Entech | 2016-05-18 |  | SORT-00001076
00001077 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Tubman Center - Grassroots | 0 - Basement | electrical room | ef-2 | [13 empty] | Entech | 2016-05-18 |  | SORT-00001077
00001078 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Tubman Center - Grassroots | 0 - Basement | mechanical room | ef-4 | [13 empty] | Entech | 2016-05-18 |  | SORT-00001078
00001080 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Tubman Center - Grassroots | 0 - Basement | mechanical room | ef-1 | [13 empty] | Entech | 2016-05-18 |  | SORT-00001080
00001094 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Florence Bain Senior Center | Roof |  |  |  | penn industries | [11 empty] | Entech | 2016-05-19 |  | SORT-00001094
00001095 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Florence Bain Senior Center | Roof | [15 empty] | Entech | 2016-05-19 |  | SORT-00001095
00001096 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Florence Bain Senior Center | Roof |  |  |  | penn industries | [11 empty] | Entech | 2016-05-19 |  | SORT-00001096
00001097 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Florence Bain Senior Center | Roof | [15 empty] | Entech | 2016-05-19 |  | SORT-00001097
00001100 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Florence Bain Senior Center | Roof | [15 empty] | Entech | 2016-05-19 |  | SORT-00001100
00001101 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Florence Bain Senior Center | Roof |  |  | 105s817004-00/0000701 | cook | 80 ace 80c2b | 115 |  |  | 0.167 |  |  |  | 1725 |  |  | Entech | 2016-05-19 |  | SORT-00001101
00001102 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Florence Bain Senior Center | Roof |  |  | 12711721 1201 | Dayton | 4yc86g | [10 empty] | Entech | 2016-05-19 |  | SORT-00001102
00001103 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Florence Bain Senior Center | Roof | [15 empty] | Entech | 2016-05-19 |  | SORT-00001103
00001120 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Florence Bain Senior Center | Exterior |  |  |  | Penn Ventilator | [11 empty] | Entech | 2016-05-19 |  | SORT-00001120
00000231 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - EXHAUST - AXIAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - EXHAUST - AXIAL | Alpha Ridge Maze / Storage Building | 1 - First Floor |  | f-4, marathon motor | 11151819 0801 | greenheck | se1-14-432-a4 | 115 |  |  | 1\4 |  |  | 1 | 1725 |  |  | Entech | 2016-04-20 |  | SORT-00000231
00000239 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - EXHAUST - AXIAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - EXHAUST - AXIAL | Alpha Ridge Pump Building | 1 - First Floor |  | f-5, marathon motor | 11151820 0801 | greenheck | se1-14-432-a4 | 115 |  |  | 1\4 |  |  | 1 | 1725 |  |  | Entech | 2016-04-20 |  | SORT-00000239
00000877 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - EXHAUST - DOME | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - EXHAUST - DOME | Old West Friendship Firehouse | Roof |  | NAMEPLATE FADED |  | LOREN COOK | [11 empty] | Entech | 2016-05-11 |  | SORT-00000877
00000878 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - EXHAUST - DOME | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - EXHAUST - DOME | Old West Friendship Firehouse | Roof |  |  |  | LOREN COOK | [11 empty] | Entech | 2016-05-11 |  | SORT-00000878
00000276 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - OTHER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Chemical Exposure Building | Roof |  | F-1, vektor | 11738191 0905 | greenheck | vk-h-9-a7-x | [7 empty] | 4050 |  |  | Entech | 2016-04-21 |  | SORT-00000276
00000364 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - OTHER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - OTHER | Alpha Ridge Administration Building | 1 - First Floor | elevator machine room |  |  | penn barry | ZPR0133L06AB38652 | [10 empty] | Entech | 2016-05-02 |  | SORT-00000364
00000916 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - OTHER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - OTHER | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room | sf 79 | [13 empty] | Entech | 2016-05-17 |  | SORT-00000916
00000283 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Alpha Ridge Administration Building | 1 - First Floor | sprinkler shutoff room |  | f0aa86377 | penn barry | p10v/ra | 115 |  |  | 1/30 |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000283
00000284 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Alpha Ridge Administration Building | 1 - First Floor | fire alarm annuciator room | f-3 |  | Penn Ventilator | p10ra | 115 |  |  | 1/30 |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000284
00000303 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Alpha Ridge Hogans Alley Structure 2 | 1 - First Floor |  | f-23 | 11151823 0801 | greenheck | se1-12-426-d | 115 | [5 empty] | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000303
00000304 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Alpha Ridge Hogans Alley Structure 3 | 1 - First Floor |  | f-6 | 111517260801 | greenheck | se1-12-426-d | 115 | [5 empty] | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000304
00000307 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Alpha Ridge Hogans Alley Structure 3 | 1 - First Floor |  | f-7 | 11151728 0801 | greenheck | se1-12-426-d | 115 | [5 empty] | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000307
00000308 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Alpha Ridge Hogans Alley Structure 3 | 1 - First Floor |  | f-8 | 11151727 0801 | greenheck | se1-12-426-d | 115 | [5 empty] | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000308
00000314 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Alpha Ridge Kennel | 1 - First Floor | corridor | f-10, exhaust fan 17, asco motor mdl 71636832 | 11151822 0801 | greenheck | se1-8-428-p | 115 |  |  | 1\40 |  |  | 1 | 1550 |  |  | Entech | 2016-04-21 |  | SORT-00000314
00000322 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Alpha Ridge Fire Grounds Building | 1 - First Floor | 113 | fan 2,3 | 11151725 0801 | greenheck | se1-8-440-d | 115 | [5 empty] | 1 | 1550 |  |  | Entech | 2016-04-22 |  | SORT-00000322
00000324 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Alpha Ridge Fire Grounds Building | 1 - First Floor | 108 | f-1 | 111151723 0801 | greenheck | se1-8-440-g | [6 empty] | 1 |  |  |  | Entech | 2016-04-22 |  | SORT-00000324
00000340 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Alpha Ridge Fire Grounds Building | 1 - First Floor | 112 | exhaust fan 3 | 111151724 0801 | greenheck | se1-8-440-d | 115 | [5 empty] | 1 | 1550 |  |  | Entech | 2016-04-22 |  | SORT-00000340
00000457 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Alpha Ridge Simulation Training Building | 2 - Second Floor | 210 mechanical room | f-9 | 11151621 0801 | greenheck | se1-12-432-g | [10 empty] | Entech | 2016-05-03 |  | SORT-00000457
00000494 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Alpha Ridge Landfill - Shop | 1 - First Floor | rain water harvest |  |  | Dayton | mta402 | [10 empty] | Entech | 2016-05-03 |  | SORT-00000494
00000689 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Glenwood Library | 2 - Second Floor | mechanical mezzanine 1 | ef-5 |  | Penn Ventilator | p16ra | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000689
00000737 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Glenwood Community Center | 2 - Second Floor | mechanical | ef-1 |  | Penn Ventilator | p12-ra | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000737
00000774 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Glenwood Community Center | 1 - First Floor | electrical room 155 | ef-6 |  | Penn Ventilator | p12ra | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000774
00000776 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Glenwood Community Center | 1 - First Floor | mechanical room | ef-2 |  | Penn Ventilator | p10ra | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000776
00000880 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Old West Friendship Firehouse | 1 - First Floor | GARAGE | NO NAMEPLATE | [13 empty] | Entech | 2016-05-11 |  | SORT-00000880
00001135 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304007 : FAN - PROPELLER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - PROPELLER | Florence Bain Senior Center | 0 - Ground Floor | mechanical | [14 empty] | Entech | 2016-05-19 |  | SORT-00001135
00000892 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304099 : FAN - SUPPLY - CENTRIFUGAL | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Scaggsville Public Safety Complex | Roof |  | ref-6 | rrc286203 | acme | prn100 | [10 empty] | Entech | 2016-05-17 |  | SORT-00000892
00000277 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304099 : OTHER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - CENTRIFUGAL | Alpha Ridge Chemical Exposure Building | Roof |  | F-1a, vektor, fan supply other | 11738192 0905 | greenheck | vk-h-9-x1 | [7 empty] | 4050 |  |  | Entech | 2016-04-21 |  | SORT-00000277
00000334 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304099 : OTHER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - OTHER | Alpha Ridge Fire Grounds Building | 2 - Second Floor | mezzanine | fan circulating |  | Dayton |  | 115 | [5 empty] | 1 |  |  |  | Entech | 2016-04-22 |  | SORT-00000334
00000848 | FANE | Q | UJPH-1027Q | D3040 : Distribution Systems | D304099 : OTHER | D3040 : DISTRIBUTION SYSTEMS | D304007 : FAN - OTHER | Glenwood Fire Station No. 13 | 1 - First Floor | KITCHEN | 788 CFM |  | CAPTIVE - AIRE | 3347 BD-2 | [10 empty] | Entech | 2016-05-11 |  | SORT-00000848
00000310 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Alpha Ridge Kennel | 1 - First Floor | closet | fcu1 | S0908A67609 | Carrier | FX4CNF018000AAAA | 208/230 |  |  | 1/3 |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000310
00000745 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor | fcu149 | w05l61046 | Trane | geca01511g01a000c11000b10021r000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000745
00000752 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor | fcu138 | w05l61058 | Trane | geca00911g01a000c11000b10021r000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000752
00000777 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor | fcu #6 | w05l61044 | Trane | geca01511g01a000c11000b10021r000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000777
00000778 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor | fcu#5 m.h. | w05l61054 | Trane | geca00911g01a000c11000b10021l000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000778
00000779 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor | fcu#4 m.h. | w05l61040 | Trane | geca00911g01a000c11000b10021r000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000779
00000780 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor | fcu#3 m.h. | w05l61051 | Trane | geca00911g01a000c11000b10021l000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000780
00000781 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor | fcu#2 m.h. | w05l61038 | Trane | geca00911g01a000c11000b10021r000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000781
00000782 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor | fcu#1 m.h. | w05l61059 | Trane | geca00911g01a000c11000b10021r000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000782
00000783 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor 192 | fcu#1 192 | w05l61039 | Trane | geca00911g01a000c11000b10021r000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000783
00000784 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor 192 | fcu#2 192 | w05l61050 | Trane | geca00911g01a000c11000b10021l000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000784
00000785 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor 192 | fcu#3 192 | w05l61057 | Trane | geca00911g01a000c11000b10021r000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000785
00000786 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor 192 | fcu#4 192 | w05l61036 | Trane | geca00911g01a000c11000b10021l000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000786
00000787 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor 185 | fcu#1 185 | w05l61055 | Trane | geca00911g01a000c11000b10021r000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000787
00000788 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor 185 | fcu#2 185 | w05l61034 | Trane | geca00911g01a000c11000b10021l000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000788
00000789 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor 185 | fcu#3 185 | w05l61033 | Trane | geca00911g01a000c11000b10021l000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000789
00000790 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor 182 | fcu 182 | w05l61045 | Trane | geca00911g01a000c11000b10021r000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000790
00000799 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | fire place lounge | fcu #1 f.p | w05l61053 | Trane | geca00911g01a000c11000b10021l000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000799
00000800 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | fire place lounge | fcu #2 f.p | w05l61042 | Trane | geca00911g01a000c11000b10021r000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000800
00000807 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor 105 | fcu 105 | w05l61049 | Trane | geca01511g01a000c11000b10021l000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000807
00000808 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor 169 | fcu 169 | w05l61041 | Trane | geca00911g01a000c11000b10021r000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000808
00000809 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor 116 | fcu 116 | w05l61052 | Trane | geca00911g01a000c11000b10021l000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000809
00000812 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | office 102 | fcu 102 | w05l61043 | Trane | geca01511g01a000c11000b10021r000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000812
00000817 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor 129 | fcu #1 129 | w05l61056 | Trane | geca00911g01a000c11000b10021r000000 | [7 empty] | 1 |  |  | Entech | 2016-05-06 |  | SORT-00000817
00000818 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Glenwood Community Center | 1 - First Floor | corridor 129 | fcu #2 129 | w05l61035 | Trane | geca00911g01a000c11000b10021l000000 | [7 empty] | 1 |  |  | Entech | 2016-05-06 |  | SORT-00000818
00000951 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 1 - First Floor | storage room |  |  | enviro-tec | vfrwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000951
00000952 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 1 - First Floor | arson unit |  |  | envirotec | vrfwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000952
00000953 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 1 - First Floor | arson unit | v208 |  | enviro-tec | vfrwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000953
00000956 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | conference |  |  | enviro-tec | vfrwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000956
00000957 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | conference |  |  | enviro-tec | vfrwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000957
00000958 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | investigation unit | V212 |  | enviro-tec | vfrwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000958
00000959 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | investigation unit |  |  | enviro-tec | vfrwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000959
00000960 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | interview room 3 | v215 |  | enviro tec | vrfwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000960
00000961 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | administrative support | v216 |  | enviro tec | vrfwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000961
00000962 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | traffic safety | v206 |  | enviro tec | vrfwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000962
00000963 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | traffic safety | v204; 0604b size |  | enviro tec | vrfwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000963
00000964 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | traffic safety | v203 |  | enviro tec | vrfwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000964
00000965 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | special operations | v201; size 0806b |  | enviro tec | vrfwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000965
00000966 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | special operations |  |  | enviro tec | vrfwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000966
00000967 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | secondary dispatch |  |  | enviro tec | vrfwc | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000967
00000980 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | exercise room |  |  | enviro-tec | vrfwc | [10 empty] | Entech | 2016-05-18 |  | SORT-00000980
00000983 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | mens locker room | fv402 |  | enviro-tec | vvfwcii | [6 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000983
00000984 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | 110 debriefing |  |  | enviro-tec | vvfwcii | [6 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000984
00000985 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | lounge | 110 |  | enviro-tec | vvfwcii | [6 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000985
00000986 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | lounge | 016 |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000986
00000987 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | lounge | fv402 |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000987
00000988 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | corridor |  |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000988
00000989 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | corridor |  |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000989
00000990 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | corridor | fv402 |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000990
00000991 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | corridor | tag 91 |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000991
00000992 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | mens room |  |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000992
00000993 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | mens room | 61,65,69 |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000993
00000996 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | corridor |  |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000996
00000997 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | corridor | lock box room |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000997
00000998 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | computer ops |  |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000998
00000999 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | computer ops |  |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000999
00001000 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | duty officers |  |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00001000
00001001 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | duty officers | tag 030 |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00001001
00001002 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | duty officers | tag 42,43 |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00001002
00001003 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | duty officers | rag 45,46,47 |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00001003
00001004 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | duty officers |  |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 | 1 |  |  | Entech | 2016-05-18 |  | SORT-00001004
00001005 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | duty officers |  |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 | 1 |  |  | Entech | 2016-05-18 |  | SORT-00001005
00001006 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | cooridor outside lobby |  |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 | 1 |  |  | Entech | 2016-05-18 |  | SORT-00001006
00001018 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | firestation corridor |  |  | international environmental | [11 empty] | Entech | 2016-05-18 |  | SORT-00001018
00001019 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | locker room |  |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00001019
00001020 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | locker room | tag 002 |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00001020
00001021 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | locker room | tag 96,97 |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00001021
00001022 | FCU | SA,A | UJPH-1012SA, UJPH-1012A | D3050 : Terminal and Package Units | D305003 : FAN COIL UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305003 : FAN COIL UNIT | Scaggsville Public Safety Complex | 0 - Ground Floor | office area | tag |  | enviro-tec | vvfwcii | 277 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00001022
00001065 | FILTER | Q | UJPH-5025Q | D3090 : Other HVAC Systems and Equipment |  | D3040 : DISTRIBUTION SYSTEMS | D304006 : CHILLED WATER DISTRIBUTION SYSTEMS | Tubman Center - Grassroots | 0 - Basement | mechanical room | cooloing tower filter | 40768-015 | lakos | il-0300-8 | [10 empty] | Entech | 2016-05-18 |  | SORT-00001065 | Will adjust frequency based on purged sediment volume
00001111 | FTH | A | UJPH-1094A | D3020 : Heat Generating Systems | D302099 : OTHER | D3050 : TERMINAL AND PACKAGE UNITS | D305004 : FIN TUBE RADIATION | Florence Bain Senior Center | 0 - Ground Floor | tea room | electric finn tube | [13 empty] | Entech | 2016-05-19 |  | SORT-00001111
00001138 | FTH | A | UJPH-1094A | D3020 : Heat Generating Systems | D302099 : OTHER | D3050 : TERMINAL AND PACKAGE UNITS | D305004 : FIN TUBE RADIATION | Florence Bain Senior Center | 0 - Ground Floor | corridor | elec finn tube | [13 empty] | Entech | 2016-05-19 |  | SORT-00001138
00001139 | FTH | A | UJPH-1094A | D3020 : Heat Generating Systems | D302099 : OTHER | D3050 : TERMINAL AND PACKAGE UNITS | D305004 : FIN TUBE RADIATION | Florence Bain Senior Center | 0 - Ground Floor | corridor | elec finn tube | [13 empty] | Entech | 2016-05-19 |  | SORT-00001139
00000325 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Alpha Ridge Fire Grounds Building | 2 - Second Floor |  | mezzanine, gas fired, gf-1 | S1008A03875 | Carrier | 58mxb120-f-11120 | 115 |  |  | 3/4 |  |  | 1 |  | 112000 |  | Entech | 2016-04-22 |  | SORT-00000325
00000327 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Alpha Ridge Fire Grounds Building | 2 - Second Floor |  | mezzanine, gas fired, gf-1a | S1008A03882 | Carrier | 58mxb120-f-11120 | 115 |  |  | 3/4 |  |  | 1 |  | 112000 |  | Entech | 2016-04-22 |  | SORT-00000327
00000330 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Alpha Ridge Fire Grounds Building | 2 - Second Floor |  | mezzanine, gas fired, gf-2 | 0908a02918 | Carrier | 58mxb080-f-11116 | 115 |  |  | 1/2 |  |  | 1 |  | 75000 |  | Entech | 2016-04-22 |  | SORT-00000330
00000331 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Alpha Ridge Fire Grounds Building | 2 - Second Floor |  | mezzanine, gas fired, gf-2a | 0908a02849 | Carrier | 58mxb080-f-11116 | 115 |  |  | 1/2 |  |  | 1 |  | 75000 |  | Entech | 2016-04-22 |  | SORT-00000331
00000452 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Alpha Ridge Simulation Training Building | 2 - Second Floor | mechanical room |  | S4413A54471 | Carrier | ZI59SC2B120S241122 | [7 empty] | 1 | 112000 |  | Entech | 2016-05-03 |  | SORT-00000452
00000454 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Alpha Ridge Simulation Training Building | 2 - Second Floor | 210 mechanical room | unit 4 | 0908a02916 | Carrier | 58mxb080-f-11116 | [6 empty] | 1 |  | 75000 |  | Entech | 2016-05-03 |  | SORT-00000454
00000455 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Alpha Ridge Simulation Training Building | 2 - Second Floor | 210 mechanical room | unit 4a | 0908a02915 | Carrier | 58mxb080-f-11116 | [6 empty] | 1 |  | 75000 |  | Entech | 2016-05-03 |  | SORT-00000455
00000508 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Alpha Ridge Landfill - Shop | 2 - Second Floor | mezzanine south | beckett burner | r110054 | cox | ho 225 | [7 empty] | 1 |  | 224000 | Entech | 2016-05-03 |  | SORT-00000508
00000510 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Alpha Ridge Landfill - Shop | 2 - Second Floor | north mezzanine |  | l60 27299 9140 | York | p-lfb23f25001a | [9 empty] | 250000 | Entech | 2016-05-03 |  | SORT-00000510
00000587 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Western Regional Park - Concession | 0 - Ground Floor | 109 storage area | electric | 54041102v | Trane | 2tec3f48a1000aa | [6 empty] | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000587
00000589 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Western Regional Park - Concession | 0 - Ground Floor | 109 storage area | electric | 540411t2v | Trane | 2tec3f48a1000aa | [6 empty] | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000589
00000644 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Western Regional Park - Maintenance Building | 0 - Ground Floor | mechanical |  | 4607A05675 | bryant | 340aav060080absa | [6 empty] | 1 |  | 74000 |  | Entech | 2016-05-05 |  | SORT-00000644
00000826 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Glenwood Fire Station No. 13 | Mezzanine |  |  | 12154P097G | TRANE | TUH1B080A9421AA | [8 empty] | 80000 |  | Entech | 2016-05-11 |  | SORT-00000826
00000827 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Glenwood Fire Station No. 13 | Mezzanine |  |  | 12143NDC7G | TRANE | TUH1B080A9421AA | [8 empty] | 80000 |  | Entech | 2016-05-11 |  | SORT-00000827
00000828 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Glenwood Fire Station No. 13 | Mezzanine |  | #3 | 12154PW37G | TRANE | TUH1B080A9421AA | [8 empty] | 80000 |  | Entech | 2016-05-11 |  | SORT-00000828
00000829 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Glenwood Fire Station No. 13 | Mezzanine |  | #4 | 12154PU97G | TRANE | TUH1B080A9421AA | [8 empty] | 80000 |  | Entech | 2016-05-11 |  | SORT-00000829
00000830 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Glenwood Fire Station No. 13 | Mezzanine |  | GFF5 | 12153SP7G | TRANE | TUH1D120A9601AA | [8 empty] | 110000 |  | Entech | 2016-05-11 |  | SORT-00000830
00000863 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Old West Friendship Firehouse | 1 - First Floor | MECHANICAL Room | FURNACE 1 | 3693A03605 | BRYANT | 350MAV060120 |  |  | 13.4 | 0.75 |  |  | 1 |  | 120000 |  | Entech | 2016-05-11 |  | SORT-00000863
00000864 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Old West Friendship Firehouse | 1 - First Floor | MECHANICAL Room | PLUS 90 | 3793A05746 | BRYANT | 350MAV060080 |  |  | 12.2 | 0.75 |  |  | 1 |  | 80000 |  | Entech | 2016-05-11 |  | SORT-00000864
00000869 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Old West Friendship Firehouse | 1 - First Floor | GARAGE | 1 OF 2 |  | HASTINGS | [11 empty] | Entech | 2016-05-11 |  | SORT-00000869
00000870 | FURN | Q,A | UJPH-1112Q, UJPH-1112A | D3020 : Heat Generating Systems | D302003 : FURNACE | D3020 : HEAT GENERATING SYSTEMS | D302003 : FURNACE | Old West Friendship Firehouse | 1 - First Floor | GARAGE | 2 OF 2 |  | HASTINGS | [11 empty] | Entech | 2016-05-11 |  | SORT-00000870
00000248 | GENERATOR | A | UJPH-1252A | D5010 : Electrical Service and Distribution | D501099 : OTHER | D5090: OTHER ELECTRICAL SERVICES | D509002 : EMERGENCY GENERATOR - DIESEL | Alpha Ridge Administration Building | Exterior |  |  | c130468363 | cummings | dfeg-132290 | 480 |  |  |  | 437.5 | 350 | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000248 | No load bank or building transfer
00000250 | GENERATOR | A | UJPH-1252A | D5010 : Electrical Service and Distribution | D501099 : OTHER | D5090: OTHER ELECTRICAL SERVICES | D509002 : EMERGENCY GENERATOR - DIESEL | Alpha Ridge Administration Building | Exterior |  |  | i060970828 | cummings | dgfa-5775038 | 480 |  |  |  | 187.5 | 150 | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000250 | No load bank or building transfer
00000911 | GENERATOR | A | UJPH-1252A | D5090 : Other Electrical Services |  | D5090: OTHER ELECTRICAL SERVICES | D509002 : EMERGENCY GENERATOR - DIESEL | Scaggsville Public Safety Complex | Exterior |  | emergency generator | A130447101 | cummins | DFEK-1220279 | 277 |  |  |  | 625 | 500 |  |  |  |  | Entech | 2016-05-17 |  | SORT-00000911 | No load bank or building transfer
00000535 | GENERATOR | A | UJPH-1252A | D5090: Other Electrical Services | D509002 : EMERGENCY GENERATOR - GAS | D5090: OTHER ELECTRICAL SERVICES | D509002 : EMERGENCY GENERATOR - GAS | Alpha Ridge Landfill - Truck Fill Building | Exterior |  |  | e910393644 | Onan | 80dgda | 480 |  |  |  |  | 100 | 80 | 3 |  |  | Entech | 2016-05-04 |  | SORT-00000535 | No load bank or building transfer
00000608 | GENERATOR | A | UJPH-1252A | D5090: Other Electrical Services | D509002 : EMERGENCY GENERATOR - GAS | D5090: OTHER ELECTRICAL SERVICES | D509002 : EMERGENCY GENERATOR - GAS | Glenwood Community Center | Exterior |  |  | L050863723 | cummins | gghg-5745658 |  |  |  |  | 106.2 | 85 | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000608 | No load bank or building transfer
00000636 | GENERATOR | A | UJPH-1252A | D5090: Other Electrical Services | D509002 : EMERGENCY GENERATOR - GAS | D5090: OTHER ELECTRICAL SERVICES | D509002 : EMERGENCY GENERATOR - GAS | Western Regional Park - Maintenance Building | Exterior |  |  | 2101484 | Generac | 10684790100 |  |  |  |  | 169 | 135 | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000636 | No load bank or building transfer
00000849 | GENERATOR | A | UJPH-1252A | D5090: Other Electrical Services | D509002 : EMERGENCY GENERATOR - GAS | D5090: OTHER ELECTRICAL SERVICES | D509002 : EMERGENCY GENERATOR - GAS | Glenwood Fire Station No. 13 | 1 - First Floor | FIRE PUMP ROOM |  | 3029760 |  | 100REZG |  |  | 347 |  | 125 | 100 | 60 | 1800 |  |  | Entech | 2016-05-11 |  | SORT-00000849 | No load bank or building transfer
00000881 | GENERATOR | A | UJPH-1252A | D5090: Other Electrical Services | D509002 : EMERGENCY GENERATOR - GAS | D5090: OTHER ELECTRICAL SERVICES | D509002 : EMERGENCY GENERATOR - GAS | Old West Friendship Firehouse | Exterior |  |  | 268587 | KOHLER | 80RZ282 |  |  | 278 |  |  | 80 | 3 |  |  |  | Entech | 2016-05-11 |  | SORT-00000881 | No load bank or building transfer
00000439 | GENERATOR | A | UJPH-1252A | D5090: Other Electrical Services | D509002 : EMERGENCY GENERATOR - OIL | D5090: OTHER ELECTRICAL SERVICES | D509002 : EMERGENCY GENERATOR - OIL | Alpha Ridge Training Radio Facility | 1 - First Floor | generator room |  | b010210215 | Onan | dgda-4955692 |  |  |  |  | 100 | 80 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000439 | No load bank or building transfer
00000247 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - CONDENSER | Alpha Ridge Administration Building | Exterior |  |  |  | mitSUBISHI | puz-a36nha | 208/230 |  | 30 |  |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000247
00000256 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - CONDENSER | Alpha Ridge Administration Building | Low Roof |  | shp-2 | 52uoo1420 | mitSUBISHI | puz-a36nha | 208/230 |  | 30 |  |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000256
00000268 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - CONDENSER | Alpha Ridge Chemical Exposure Building | Exterior |  |  | 4609e10539 | Carrier | 25hbb324w300 | 208/230 |  | 0.75 | 1/10 |  |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000268
00000430 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - CONDENSER | Alpha Ridge Police Pistol Range | Exterior |  |  | 309j133042997-02 | bard | w3a62-a15 | 230/208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000430
00000431 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - CONDENSER | Alpha Ridge Police Pistol Range | Exterior |  |  | 309j133042996-02 | bard | w3a62-a15 | 230/208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000431
00000432 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - CONDENSER | Alpha Ridge Training Radio Facility | Exterior |  |  | 153 001542380-02 | bard | wa602-a1xwxxxj | 230/208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000432
00000433 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - CONDENSER | Alpha Ridge Training Radio Facility | Exterior |  |  | 153 001542381-02 | bard | wa602-a1xwxxxj | 230/208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000433
00000476 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - CONDENSER | Alpha Ridge Landfill - Trailer | Exterior |  |  | 309h122914658-02 | bard | w36a1-a10xx4xxx | [10 empty] | Entech | 2016-05-03 |  | SORT-00000476
00000477 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - CONDENSER | Alpha Ridge Landfill - Trailer | Exterior |  |  | 309j12931853-02 | bard | w36a1-a10xx4xxx | [10 empty] | Entech | 2016-05-03 |  | SORT-00000477
00000484 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - CONDENSER | Alpha Ridge Landfill - Shop | Exterior |  |  | a000511 | daikin | reyq96pbtj | [7 empty] | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000484
00000555 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - CONDENSER | Alpha Ridge Landfill - Weigh Station | Exterior |  |  | dnn001413 | fujitsu | aou9r2 | [6 empty] | 1 | 1 |  |  | Entech | 2016-05-04 |  | SORT-00000555
00000583 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - CONDENSER | Western Regional Park - Concession | Exterior |  |  | 53557ek4f | Trane | 2twa0048a4000ab | [6 empty] | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000583
00000584 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - CONDENSER | Western Regional Park - Concession | Exterior |  |  | 53557gf4f | Trane | 2twa0048a4000ab | [6 empty] | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000584
00000973 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Scaggsville Public Safety Complex | 0 - Ground Floor | it closet |  | 24m01700 | mitsubishi | pka-a24ka4 | [6 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000973
00001107 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | corridor | hp1 ckt 5 | w04d18220 | Trane | geca01211e011000d20000a10012L000000 | 208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-19 |  | SORT-00001107
00001108 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | office area | hp-1 lh | w04d18229 | Trane | geca01811e011000d20000a10012L000000 | 208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-19 |  | SORT-00001108
00001109 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | office area | hp1 ckt 15 | w04d18222 | Trane | geca0091e011000d20000a10012L000000 | 208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-19 |  | SORT-00001109
00001110 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | office area | hp3-lh | w04d18224 | Trane | geca0091e011000d20000a10012L000000 | 208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-19 |  | SORT-00001110
00001112 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | office area | hp3-lh | w04d18226 | Trane | geca0091e011000d20000a10012L000000 | 208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-19 |  | SORT-00001112
00001113 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | office area | hp3-lh | w04d18223 | Trane | geca0091e011000d20000a10012L000000 | 208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-19 |  | SORT-00001113
00001114 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | office area | hp3-lh | w04d18225 | Trane | geca0091e011000d20000a10012L000000 | 208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-19 |  | SORT-00001114
00001115 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | office area | hp3-lh | w04d18227 | Trane | geca0091e011000d20000a10012L000000 | 208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-19 |  | SORT-00001115
00001116 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | office area | hp1-lh | w04d18230 | Trane | geca0181e011000d20000a10012L000000 | 208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-19 |  | SORT-00001116
00001117 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | office area |  |  | Trane | geca0091e011000d20000a10012L000000 | 208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-19 |  | SORT-00001117
00001141 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | computer lab | [14 empty] | Entech | 2016-05-19 |  | SORT-00001141
00001142 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | exercise room |  |  | Trane | [7 empty] | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001142
00001143 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | pottery room |  |  | Trane | [7 empty] | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001143
00001144 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | storage room |  |  | Trane | geca0091e011000d20000a10012L000000 | 208 | [5 empty] | 1 |  |  |  | Entech | 2016-05-19 |  | SORT-00001144
00001145 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | wood shop | [14 empty] | Entech | 2016-05-19 |  | SORT-00001145
00001149 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | multipurpose room 3 |  |  | Trane | [7 empty] | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001149
00001150 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | multipurpose room 2 |  |  | Trane | [7 empty] | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001150
00001151 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | multipurpose room 3 |  |  | Trane | [7 empty] | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001151
00001152 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | kitchen |  |  | Trane | [11 empty] | Entech | 2016-05-19 |  | SORT-00001152
00001153 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | pantry kitchen | hp-5 | [13 empty] | Entech | 2016-05-19 |  | SORT-00001153
00001154 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3020 : Heat Generating Systems | D302005 : PUMP - HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Florence Bain Senior Center | 0 - Ground Floor | meeting room |  |  | Trane | [11 empty] | Entech | 2016-05-19 |  | SORT-00001154
00000801 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D302005 : PUMP - WATER SOURCE HEAT | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 177 | water source heat pump, mr 177 | w05m64963 | Trane | gevb03641m01a0tlc010000100001000000 | [6 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000801
00000724 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 2 - Second Floor | mechanical | water source heat pump, mezz 3 | w05m64960 | Trane | gevb01811m01a0tlc010000100001000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000724
00000725 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 2 - Second Floor | mechanical | water source heat pump, mezz 3 | w14a00492 | Trane | gevb01811e01a0tr0010000100000000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000725
00000727 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 2 - Second Floor | mechanical | water source heat pump, mezz 1 | w05m64970 | Trane | gevb06041m02a0trc010000100001000000 | [6 empty] | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000727
00000743 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 142 | water source heat pump, mr 142 | w05m64959 | Trane | [7 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000743
00000744 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 141 | water source heat pump, mr 141 | w06h48312 | Trane | gevb806041n02a0trc010000100001000000 | [6 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000744
00000753 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 134 | water source heat pump, mr 134 #1 | w05m64446 | Trane | gevb09041d0ba0tbc01000010000000000 | [6 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000753
00000754 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 134 | water source heat pump, mr 134 #2 | w05m64445 | Trane | [7 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000754
00000791 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 194 | water source heat pump, mr 194 | w05m64968 | Trane | gevb04241m02a0tlc010000100001000000 | [6 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000791
00000792 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 190 | water source heat pump, mr 190 | w05m64969 | Trane | gevb06041m02a0trc010000100001000000 | [6 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000792
00000793 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 189 | water source heat pump, mr 189 | w05m64972 | Trane | gevb06041m02a0tlc010000100001000000 | [6 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000793
00000794 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 187 | water source heat pump, mr 187 | w05m64974 | Trane | gevb06041m02a0tlc010000100001000000 | [6 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000794
00000802 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 176 | water source heat pump, mr 176 | w06f30952 | Trane | gevb03641n01a0trc010000100001000000 | [6 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000802
00000810 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 104 | water source heat pump, mr 104 | w05m64962 | Trane | gevb02441m01a0tlc010000100001000000 | [6 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000810
00000811 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 100 | water source heat pump, mr 100 | w05m64966 | Trane | gevb0424m02a0trc010000100001000000 | [6 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000811
00000813 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 114 | water source heat pump, mr 114 | w05m64958 | Trane | gevb01811m01a0tlc010000100001000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000813
00000814 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 113 | water source heat pump, mr 113 | w05m64955 | Trane | gevb01511m01a0trc010000100001000000 | [7 empty] | 1 |  |  | Entech | 2016-05-06 |  | SORT-00000814
00000815 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 163 | water source heat pump, mr 163 | w05m64957 | Trane | gevb01811m01a0trc010000100001000000 | [7 empty] | 1 |  |  | Entech | 2016-05-06 |  | SORT-00000815
00000816 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 117 | water source heat pump, mr 117 | w05m64961 | Trane | gevb0244m01a0tlc010000100001000000 | [7 empty] | 3 |  |  | Entech | 2016-05-06 |  | SORT-00000816
00000819 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 128 | water source heat pump, mr 128 | w05m64971 | Trane | gevb0604m02a0tlc010000100001000000 | [7 empty] | 3 |  |  | Entech | 2016-05-06 |  | SORT-00000819
00000820 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | mechanical 127 | water source heat pump, mr 127 | w05m64967 | Trane | gevb0424m02a0trc010000100001000000 | [7 empty] | 3 |  |  | Entech | 2016-05-06 |  | SORT-00000820
00001029 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Tubman Center - Grassroots | attic |  | wshp-9 | w07g49028 | Trane | gehb09031d0e00rld0100002000000000000 | 208 | [5 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001029
00001030 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Tubman Center - Grassroots | attic |  | wshp-4 | W07G49025 | Trane | gehb09031d0e00rld0100002000000000000 | 208 | [5 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001030
00001031 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Tubman Center - Grassroots | attic |  | wshp-8 | W07G49027 | Trane | gehb07231d0c00rld0100002000000000000 | 208 | [5 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001031
00001034 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Tubman Center - Grassroots | attic |  | wshp-7 | W07G49026 | Trane | gehb09031d0d00lrd0100001000000000000 | 208 | [5 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001034
00001035 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Tubman Center - Grassroots | attic |  | wshp-2 | W07H56303 | Trane | gehb03611t0200rld0100001000000000000 | 208 | [5 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001035
00001036 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Tubman Center - Grassroots | attic |  | wshp-3 | w07g49024 | Trane | gehb07231d0c00rld0100001000000000000 | 208 | [5 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001036
00001037 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Tubman Center - Grassroots | attic |  | wshp-1 | w07h56302 | Trane | gehb04811t0200rld0100001000000000000 | 208 | [5 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001037
00001038 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Tubman Center - Grassroots | attic |  | wshp-6 | w07h56305 | Trane | gehb04811t0200rld0100001000000000000 | 208 | [5 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001038
00001039 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Tubman Center - Grassroots | attic |  | wshp-5 | w07h56304 | Trane | gehb04811t0200rld0100001000000000000 | 208 | [5 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001039
00001046 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Tubman Center - Grassroots | 1 - First Floor | exterior mechanical room | wshp-12 | w07g49029 | Trane | gevb07211d0a00tb0100002000000000000 | 208 | [5 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001046
00001082 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Tubman Center - Grassroots | 2 - Second Floor | 202 | wshp-10 | w07h56305 | Trane | gevb03611t0200tld0100001000000000000 | 208 | [5 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001082
00001084 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Tubman Center - Grassroots | 1 - First Floor | 126 | wshp-11 | w07h56307 | Trane | gevb04811t0200tld0100001000000000000 | 208 | [5 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001084
00001085 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3040 : Distribution Systems | D304099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Tubman Center - Grassroots | 1 - First Floor | elevator machine room | wshp-13 | w07h56308 | Trane | gevb03611ta100tld0100001000000000000 | 208 | [5 empty] | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001085
00001062 | HTEX | A | UGSA-HVAC-HXR-01-01Y | D3020 : Heat Generating Systems | D302001 : HEAT EXCHANGER - PLATE N FRAME | D3020 : HEAT GENERATING SYSTEMS | D302001 : HEAT EXCHANGER - PLATE N FRAME | Tubman Center - Grassroots | 0 - Basement | mechanical room |  | sp 327 | tranter | gxd-026-l-5-uj-33 | [10 empty] | Entech | 2016-05-18 |  | SORT-00001062
00001129 | HTEX | A | UGSA-HVAC-HXR-01-01Y | D3020 : Heat Generating Systems | D302001 : HEAT EXCHANGER - PLATE N FRAME | D3020 : HEAT GENERATING SYSTEMS | D302001 : HEAT EXCHANGER - PLATE N FRAME | Florence Bain Senior Center | 0 - Ground Floor | mechanical |  | p25996h | superchanger | ux-216-hp-145 | [10 empty] | Entech | 2016-05-19 |  | SORT-00001129
00000874 | HUMID | A | UJPH-1035A-E | D3040 : Distribution Systems | D304099 : OTHER | D3040 : DISTRIBUTION SYSTEMS | D304001 : AIR DISTRIBUTION, HEATING, AND COOLING - HUMIDIFIER | Old West Friendship Firehouse | 2 - Second Floor | Electrical CLOSET | HUMIDIFIER | 106GI3592497 | APRILAIRE | 440 |  |  | 0.7 | [7 empty] | Entech | 2016-05-11 |  | SORT-00000874
00000875 | HUMID | A | UJPH-1035A-E | D3040 : Distribution Systems | D304099 : OTHER | D3040 : DISTRIBUTION SYSTEMS | D304001 : AIR DISTRIBUTION, HEATING, AND COOLING - HUMIDIFIER | Old West Friendship Firehouse | 2 - Second Floor | Electrical CLOSET | HUMIDIFIER | 109FI3586820 | APRILAIRE | 440 |  |  | 0.7 | [7 empty] | Entech | 2016-05-11 |  | SORT-00000875
00000264 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Alpha Ridge Apparatus Storage Building | 1 - First Floor | electrical room |  | ge 0507d25623 | General Electric | ge30s06aag | 240/208 | [5 empty] | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000264
00000273 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Alpha Ridge Chemical Exposure Building | 1 - First Floor | bay b | 50 gal | 0827A017878 | State | ES652DORT | 208/240 |  |  |  |  | 4.5 | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000273
00000311 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Alpha Ridge Kennel | 1 - First Floor | closet | 30 gal | L07A126511 | State | ES630DORT | 240/208 |  |  |  |  | 4.5 | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000311
00000320 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Alpha Ridge Fire Grounds Building | 1 - First Floor | 113 |  | 0945j011783 | state select | es66s0msk 200 | 120 |  |  |  |  | 1.65 | 1 |  |  |  | Entech | 2016-04-22 |  | SORT-00000320
00000375 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Alpha Ridge Administration Building | 1 - First Floor | janitor |  | f06m003628 | A O Smith | den 66 110 | 480 |  |  |  |  | 8 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000375
00000383 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Alpha Ridge Administration Building | 1 - First Floor | 165 janitor |  | sg061129343 | A O Smith | dve 300 | 480 |  | 55 |  |  | 45 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000383
00000466 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Alpha Ridge Park - Comfort Station | 1 - First Floor | janitor | 30 gal | 1420M001738 | A O Smith | DEN 30 110 | [5 empty] | 9 | 3 |  |  |  | Entech | 2016-05-03 |  | SORT-00000466
00000479 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Alpha Ridge Landfill - Trailer | 1 - First Floor | closet | 80 gal | JA16082400 | Bradford White | m280r6ds-1ncww | [7 empty] | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000479
00000511 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Alpha Ridge Landfill - Shop | 2 - Second Floor | north mezzanine |  | mb95-0409023-916 | A O Smith | dre 52 916 | [6 empty] | 15 | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000511
00000550 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Alpha Ridge Landfill - Transfer Station Control Building | 0 - Ground Floor | restroom | 10 gal | m03409568 | State | cpe1010msa | [10 empty] | Entech | 2016-05-04 |  | SORT-00000550
00000567 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Alpha Ridge Landfill - Weigh Station | 0 - Ground Floor | electrical room |  | gc02-0512846-917 | A O Smith | ees 40 917 | [10 empty] | Entech | 2016-05-04 |  | SORT-00000567
00000586 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Western Regional Park - Concession | 0 - Ground Floor | 103 janitors closet | 30 gal | 1533M003016 | A O Smith | DEN 30 110 | [5 empty] | 10 | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000586
00000627 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | janitor | 30 gal | 1101m001541 | A O Smith | den 30 110 | [5 empty] | 9 | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000627
00000631 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Western Regional Park - Comfort Station 2 | 0 - Ground Floor | janitor |  | 1102m000314 | A O Smith | den 30 110 | [5 empty] | 9 | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000631
00000643 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Western Regional Park - Maintenance Building | 0 - Ground Floor | mechanical | 50 gal | 1537A015253 | A O Smith | ENT 50 100 | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000643
00000679 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Glenwood Library | 1 - First Floor | mechanical mezzanine 2 | 30 gal | 1403A25507 | A O Smith | ECL 30 200 | 240/208 |  |  |  |  | 4.5 | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000679
00000702 | HWH | A | UJPH-1131A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - ELEC | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - ELECTRIC | Glenwood Library | 1 - First Floor | mechanical | 30 gal | 1328A004546 | A O Smith | ECL 30 200 | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000702
00000333 | HWH | Q,A | UJPH-1133Q, UJPH-1133A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - GAS | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - GAS | Alpha Ridge Fire Grounds Building | 2 - Second Floor | mezzanine | gas, propane | L07A090691 | state select | GS630HBRT | 120 |  |  |  |  | 1.65 | 1 |  |  |  | Entech | 2016-04-22 |  | SORT-00000333
00000732 | HWH | Q,A | UJPH-1133Q, UJPH-1133A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - GAS | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - GAS | Glenwood Community Center | 2 - Second Floor | mechanical |  | 1318M000220 | A O Smith | BTH 400A 104 | [8 empty] | 399900 |  | Entech | 2016-05-05 |  | SORT-00000732
00000823 | HWH | Q,A | UJPH-1133Q, UJPH-1133A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - GAS | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - GAS | Glenwood Fire Station No. 13 | Mezzanine |  | 70000 BTUH Input, 75 gal | 1140A015241 | State | SDV757ONE 200 | 120 | [5 empty] | 1 |  |  |  | Entech | 2016-05-11 |  | SORT-00000823
00000865 | HWH | Q,A | UJPH-1133Q, UJPH-1133A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - GAS | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - GAS | Old West Friendship Firehouse | 1 - First Floor | MECHANICAL Room | 72.82 GPH | 1440A02280 | AO SMITH | FCG75301 | [8 empty] | 75100 |  | Entech | 2016-05-11 |  | SORT-00000865
00000917 | HWH | Q,A | UJPH-1133Q, UJPH-1133A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - GAS | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - GAS | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room |  | 0707121896 | pvi | 500p 225a-tp | 115 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000917
00001053 | HWH | Q,A | UJPH-1133Q, UJPH-1133A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - GAS | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - GAS | Tubman Center - Grassroots | 0 - Basement | mechanical room | 100 gal, wh-1 | de9141186 | locinvar | tna401-100 | 120 | [9 empty] | Entech | 2016-05-18 |  | SORT-00001053
00001054 | HWH | Q,A | UJPH-1133Q, UJPH-1133A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - GAS | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - GAS | Tubman Center - Grassroots | 0 - Basement | mechanical room | 100 gal, wh-1 | de9141187 | locinvar |  | 120 | [9 empty] | Entech | 2016-05-18 |  | SORT-00001054
00001055 | HWH | Q,A | UJPH-1133Q, UJPH-1133A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - GAS | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - GAS | Tubman Center - Grassroots | 0 - Basement | mechanical room | wh-3 | 1421M000825 | A O Smith |  | 120 | [9 empty] | Entech | 2016-05-18 |  | SORT-00001055
00001056 | HWH | Q,A | UJPH-1133Q, UJPH-1133A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - GAS | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - GAS | Tubman Center - Grassroots | 0 - Basement | mechanical room | 100 gal, wh-4 | de9039871 | locinvar |  | 120 | [9 empty] | Entech | 2016-05-18 |  | SORT-00001056
00001133 | HWH | Q,A | UJPH-1133Q, UJPH-1133A | D2020 : Domestic Water Distribution | D202003 : WTR HEATER - GAS | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : WTR HEATER - GAS | Florence Bain Senior Center | 0 - Ground Floor | mechanical |  | 1316M000702 | A O Smith | BT 100 300 | [8 empty] | 70000 |  | Entech | 2016-05-19 |  | SORT-00001133
00000927 | MCC | A | UJPH-1282A-IR | D5010 : Electrical Service and Distribution | D501007 : MOTOR CONTROL CENTER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501007 : MOTOR CONTROL CENTER | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room | model 5 |  | Square-D | Square-D | [10 empty] | Entech | 2016-05-17 |  | SORT-00000927
00000712 | POWER | A | UJPH-5026A | D5030 : Communication and Security Systems | D503099 : OTHER | D5030 : COMMUNICATION AND SECURITY SYSTEMS | D503001 : FIRE ALARM SYSTEMS - POWER SUPPLY | Glenwood Library | 1 - First Floor | electrical | fire alarm panel power module, ceberus |  | Siemens | pad-2 | [10 empty] | Entech | 2016-05-05 |  | SORT-00000712
00000769 | POWER | A | UJPH-5026A | D5030 : Communication and Security Systems | D503099 : OTHER | D5030 : COMMUNICATION AND SECURITY SYSTEMS | D503001 : FIRE ALARM SYSTEMS - POWER SUPPLY | Glenwood Community Center | 1 - First Floor | electrical room 155 | power supply |  | notifier | fcps-24s8 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000769
00000613 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D2020 : Domestic Water Distribution | D202003 : PUMP - END SUCTION | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : PUMP - END SUCTION | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | pump room | comfort station 1 |  | Taco | CI1206 |  |  |  | 7.5 |  |  | 3 | 3450 |  |  | Entech | 2016-05-04 |  | SORT-00000613
00000615 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D2020 : Domestic Water Distribution | D202003 : PUMP - END SUCTION | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : PUMP - END SUCTION | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | pump room | comfort station 2 |  | Taco | CI1206 |  |  |  | 7.5 |  |  | 3 | 3450 |  |  | Entech | 2016-05-04 |  | SORT-00000615
00000718 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D2020 : Domestic Water Distribution | D202003 : PUMP - END SUCTION | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : PUMP - END SUCTION | Glenwood Community Center | 2 - Second Floor | mechanical |  | 9bf1k2c0 | goulds | 3656 |  |  |  | 7.5 |  |  | 3 | 3450 |  |  | Entech | 2016-05-05 |  | SORT-00000718
00000680 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D2020 : Domestic Water Distribution | D202003 : PUMP - INLINE | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : PUMP - INLINE | Glenwood Library | 2 - Second Floor | mechanical mezzanine 2 | hw circulating |  | Taco | 1615c3e1l | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000680
00000682 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D2020 : Domestic Water Distribution | D202003 : PUMP - INLINE | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : PUMP - INLINE | Glenwood Library | 2 - Second Floor | mechanical mezzanine 2 | hw circulating |  | Taco | [7 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000682
00000685 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D2020 : Domestic Water Distribution | D202003 : PUMP - INLINE | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : PUMP - INLINE | Glenwood Library | 2 - Second Floor | mechanical mezzanine 1 | hw circulating |  | Taco | 1612c3n1 | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000685
00000688 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D2020 : Domestic Water Distribution | D202003 : PUMP - INLINE | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : PUMP - INLINE | Glenwood Library | 2 - Second Floor | mechanical mezzanine 1 | hw circulating |  | Taco | 1615c31s | [6 empty] | 1 | 1725 |  |  | Entech | 2016-05-05 |  | SORT-00000688
00000691 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D2020 : Domestic Water Distribution | D202003 : PUMP - INLINE | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : PUMP - INLINE | Glenwood Library | 2 - Second Floor | mechanical mezzanine 1 | hw circulating |  | Taco | 1612c3n1 | [6 empty] | 1 | 1725 |  |  | Entech | 2016-05-05 |  | SORT-00000691
00000722 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D2020 : Domestic Water Distribution | D202003 : PUMP - INLINE | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : PUMP - INLINE | Glenwood Community Center | 2 - Second Floor | mechanical | eru-3 p-7 |  | Armstrong Pumps |  |  |  |  | 1 |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000722
00000723 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D2020 : Domestic Water Distribution | D202003 : PUMP - INLINE | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : PUMP - INLINE | Glenwood Community Center | 2 - Second Floor | mechanical | eru-4 p-8 |  | Armstrong Pumps |  |  |  |  | 1 |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000723
00000726 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D2020 : Domestic Water Distribution | D202003 : PUMP - INLINE | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : PUMP - INLINE | Glenwood Community Center | 2 - Second Floor | mechanical |  |  | Armstrong Pumps |  |  |  |  | 1 |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000726
00000746 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D2020 : Domestic Water Distribution | D202003 : PUMP - INLINE | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : PUMP - INLINE | Glenwood Community Center | 1 - First Floor | corridor | [14 empty] | Entech | 2016-05-06 |  | SORT-00000746
00001069 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D2090 : Other Plumbing Systems | D209099 : OTHER | D2040 : RAIN WATER DRAINAGE | D204003 : RAIN WATER DRAINAGE EQUIPMENT - SUMP PUMP | Tubman Center - Grassroots | 0 - Basement | mechanical room | duplex sump pump and controller | [13 empty] | Entech | 2016-05-18 |  | SORT-00001069
00000915 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3010 : Energy Supply | D301001 : SKID - FUEL OIL PUMP | D3010 : ENERGY SUPPLY | D301001 : SKID - FUEL OIL PUMP | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room | PUMP 2 | [13 empty] | Entech | 2016-05-17 |  | SORT-00000915
00000700 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3020 : Heat Generating Systems | D302001 : PUMP - END SUCTION | D3020 : HEAT GENERATING SYSTEMS | D302001 : PUMP - END SUCTION | Glenwood Library | 1 - First Floor | mechanical |  |  | Taco | fe2508e2f1f2l0 |  |  |  | 7.5 |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000700
00000701 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3020 : Heat Generating Systems | D302001 : PUMP - END SUCTION | D3020 : HEAT GENERATING SYSTEMS | D302001 : PUMP - END SUCTION | Glenwood Library | 1 - First Floor | mechanical |  |  | Taco |  |  |  |  | 7.5 |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000701
00000705 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3020 : Heat Generating Systems | D302001 : PUMP - END SUCTION | D3020 : HEAT GENERATING SYSTEMS | D302001 : PUMP - END SUCTION | Glenwood Library | 1 - First Floor | mechanical |  |  | Taco | 121-154rp | [10 empty] | Entech | 2016-05-05 |  | SORT-00000705
00000706 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3020 : Heat Generating Systems | D302001 : PUMP - END SUCTION | D3020 : HEAT GENERATING SYSTEMS | D302001 : PUMP - END SUCTION | Glenwood Library | 1 - First Floor | mechanical | p-11 |  | Taco | 1510c3f1 | [10 empty] | Entech | 2016-05-05 |  | SORT-00000706
00000716 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3020 : Heat Generating Systems | D302001 : PUMP - END SUCTION | D3020 : HEAT GENERATING SYSTEMS | D302001 : PUMP - END SUCTION | Glenwood Library | 1 - First Floor | mechanical |  |  | Taco | [11 empty] | Entech | 2016-05-05 |  | SORT-00000716
00000734 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3020 : Heat Generating Systems | D302001 : PUMP - END SUCTION | D3020 : HEAT GENERATING SYSTEMS | D302001 : PUMP - END SUCTION | Glenwood Community Center | 2 - Second Floor | mechanical |  | 538005 | Armstrong Pumps |  |  |  |  | 50 |  |  | 3 | 3600 |  |  | Entech | 2016-05-05 |  | SORT-00000734
00000735 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3020 : Heat Generating Systems | D302001 : PUMP - END SUCTION | D3020 : HEAT GENERATING SYSTEMS | D302001 : PUMP - END SUCTION | Glenwood Community Center | 2 - Second Floor | mechanical |  | 538006 | Armstrong Pumps |  |  |  |  | 50 |  |  | 3 | 3600 |  |  | Entech | 2016-05-05 |  | SORT-00000735
00000920 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3020 : Heat Generating Systems | D302001 : PUMP - END SUCTION | D3020 : HEAT GENERATING SYSTEMS | D302001 : PUMP - END SUCTION | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room | phw-2 | 1807585 | Bell & Gossett | 1-1/28c 7.875 | [10 empty] | Entech | 2016-05-17 |  | SORT-00000920
00000921 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3020 : Heat Generating Systems | D302001 : PUMP - END SUCTION | D3020 : HEAT GENERATING SYSTEMS | D302001 : PUMP - END SUCTION | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room | phw-1, HEATING PUMP #1 | 1807584 | Bell & Gossett | 1-1/28c 7.875 | [10 empty] | Entech | 2016-05-17 |  | SORT-00000921
00000505 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3020 : Heat Generating Systems | D302001 : PUMP - fuel oil | D3020 : HEAT GENERATING SYSTEMS | D302001 : PUMP - FUEL OIL | Alpha Ridge Landfill - Shop | 1 - First Floor | stairwell |  |  | webster | [8 empty] | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000505
00001008 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3020 : Heat Generating Systems | D302001 : PUMP - INLINE | D3020 : HEAT GENERATING SYSTEMS | D302001 : PUMP - INLINE | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room | ahu pump |  | Bell & Gossett | [8 empty] | 1425 |  |  | Entech | 2016-05-18 |  | SORT-00001008
00001050 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3020 : Heat Generating Systems | D302001 : PUMP - INLINE | D3020 : HEAT GENERATING SYSTEMS | D302001 : PUMP - INLINE | Tubman Center - Grassroots | 0 - Basement | mechanical room |  | 172745lf | Bell & Gossett | 60 | [7 empty] | 1425 |  |  | Entech | 2016-05-18 |  | SORT-00001050
00001052 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3020 : Heat Generating Systems | D302001 : PUMP - INLINE | D3020 : HEAT GENERATING SYSTEMS | D302001 : PUMP - INLINE | Tubman Center - Grassroots | 0 - Basement | mechanical room |  |  | Bell & Gossett | 60 | [7 empty] | 1425 |  |  | Entech | 2016-05-18 |  | SORT-00001052
00001137 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3020 : Heat Generating Systems | D302001 : PUMP - INLINE | D3020 : HEAT GENERATING SYSTEMS | D302001 : PUMP - INLINE | Florence Bain Senior Center | 0 - Ground Floor | mechanical |  | g215451-01 L51 | Bell & Gossett | Bell & Gossett |  |  |  |  | 1.5 |  |  | 1 |  |  | Entech | 2016-05-19 |  | SORT-00001137
00000475 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Alpha Ridge Landfill - Pump Bldg | 1 - First Floor |  |  |  | gould | 3656 |  |  |  | 1.5 | [6 empty] | Entech | 2016-05-03 |  | SORT-00000475
00000533 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Alpha Ridge Landfill - Truck Fill Building | 1 - First Floor |  |  | a798f248 | itt-gould | 3196 |  |  |  |  | 15 |  |  |  | 3500 |  | Entech | 2016-05-04 |  | SORT-00000533
00000534 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Alpha Ridge Landfill - Truck Fill Building | 1 - First Floor |  |  | 969561 | gorman rupp | 83b3-b |  |  |  |  | 5 |  |  | 3 |  |  | Entech | 2016-05-04 |  | SORT-00000534
00000573 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Western Regional Park - Concession | 0 - Ground Floor | 102 mechanical |  |  | Taco | c112206 |  |  |  | 7.5 |  |  |  | 3450 |  |  | Entech | 2016-05-04 |  | SORT-00000573
00000647 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Western Regional Park - Maintenance Building | 0 - Ground Floor | mechanical | booster pump |  | gould | 10sh2k51d0 |  |  |  | 7.5 |  |  |  | 3450 |  |  | Entech | 2016-05-05 |  | SORT-00000647
00000698 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Glenwood Library | 1 - First Floor | mechanical |  |  | Taco |  |  |  |  | 10 |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000698
00000699 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Glenwood Library | 1 - First Floor | mechanical |  |  | Taco | fe2510e26g1f2l0 |  |  |  | 10 |  |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000699
00000922 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room | pch-2, CHILLED PUMP #2 | 1807573 | Bell & Gossett | 1-1/28c 7.875 | [10 empty] | Entech | 2016-05-17 |  | SORT-00000922
00000923 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room | pch-1, CHILLED PUMP #1 | 1807572 | Bell & Gossett | 1-1/28c 7.875 | [10 empty] | Entech | 2016-05-17 |  | SORT-00000923
00001058 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Tubman Center - Grassroots | 0 - Basement | mechanical room | cp-4 |  | Bell & Gossett |  |  |  |  | 7.5 |  |  |  | 1800 |  |  | Entech | 2016-05-18 |  | SORT-00001058
00001060 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Tubman Center - Grassroots | 0 - Basement | mechanical room | cp-3 | c046301-02 g70 | Bell & Gossett |  |  |  |  | 7.5 |  |  |  | 1800 |  |  | Entech | 2016-05-18 |  | SORT-00001060
00001066 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Tubman Center - Grassroots | 0 - Basement | mechanical room | cp-2 | c046302-02 h70 | Bell & Gossett |  |  |  |  | 7.5 |  |  |  | 1800 |  |  | Entech | 2016-05-18 |  | SORT-00001066
00001067 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Tubman Center - Grassroots | 0 - Basement | mechanical room | cp-1 | c046302-01 h70 | Bell & Gossett | Bell & Gossett |  |  |  | 7.5 |  |  |  | 1800 |  |  | Entech | 2016-05-18 |  | SORT-00001067
00001128 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Florence Bain Senior Center | 0 - Ground Floor | mechanical |  | 1bf019lfa11 | Bell & Gossett |  |  |  |  | 3 |  |  | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001128
00001130 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Florence Bain Senior Center | 0 - Ground Floor | mechanical |  | 1114632 | Bell & Gossett |  |  |  |  | 7.5 |  |  | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001130
00001131 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - END SUCTION | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - END SUCTION | Florence Bain Senior Center | 0 - Ground Floor | mechanical |  | 1118454 | Bell & Gossett |  |  |  |  | 7.5 |  |  | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001131
00000740 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - INLINE | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - INLINE | Glenwood Community Center | 2 - Second Floor | mechanical |  |  | Armstrong Pumps | astro 230ss | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000740
00001057 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - INLINE | D3030 : COOLING GENERATING SYSTEMS | D303001 : PUMP - INLINE | Tubman Center - Grassroots | 0 - Basement | mechanical room | booster pump | 1bl003 | Bell & Gossett |  | 115 | [9 empty] | Entech | 2016-05-18 |  | SORT-00001057
00000489 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - other | D2040 : RAIN WATER DRAINAGE | D204003 : RAIN WATER DRAINAGE EQUIPMENT - PUMP | Alpha Ridge Landfill - Shop | 1 - First Floor | rain water harvest main control panel mcp-1 |  | 12502590115 | bermad | ir-350-sr-pn 10 bsp | [10 empty] | Entech | 2016-05-03 |  | SORT-00000489
00000490 | PUMP | Q,A | UJPH-1049Q, UJPH-1049A | D3030 : Cooling Generating Systems | D303001 : PUMP - other | D2040 : RAIN WATER DRAINAGE | D204003 : RAIN WATER DRAINAGE EQUIPMENT - PUMP | Alpha Ridge Landfill - Shop | 1 - First Floor | rain water harvest main control panel mcp-1 |  |  | bermad | ir-350-sr-pn 10 bsp | [10 empty] | Entech | 2016-05-03 |  | SORT-00000490
00000251 | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | D3050 : Terminal and Package Units | D305006 : ROOFTOP UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305006 : ROOFTOP UNIT | Alpha Ridge Administration Building | Low Roof |  | rtu 6 | n0l6153070 | York | z24as74m3kdube | 460 | [5 empty] | 3 |  | 560000 |  | Entech | 2016-04-21 |  | SORT-00000251
00000252 | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | D3050 : Terminal and Package Units | D305006 : ROOFTOP UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305006 : ROOFTOP UNIT | Alpha Ridge Administration Building | Low Roof |  | rtu 5 | n0l6153071 | York | z24as44m3kdube | 460 | [5 empty] | 3 |  | 372800 |  | Entech | 2016-04-21 |  | SORT-00000252
00000257 | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | D3050 : Terminal and Package Units | D305006 : ROOFTOP UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305006 : ROOFTOP UNIT | Alpha Ridge Administration Building | Roof |  | rtu 4 | n0l6988613 | York | z24as44m3kdube | 460 | [5 empty] | 3 |  | 372800 |  | Entech | 2016-04-21 |  | SORT-00000257
00000258 | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | D3050 : Terminal and Package Units | D305006 : ROOFTOP UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305006 : ROOFTOP UNIT | Alpha Ridge Administration Building | Roof |  | rtu 3 | n0l6988614 | York | z24as44m3kdube | 460 | [5 empty] | 3 |  | 372800 |  | Entech | 2016-04-21 |  | SORT-00000258
00000280 | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | D3050 : Terminal and Package Units | D305006 : ROOFTOP UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305006 : ROOFTOP UNIT | Alpha Ridge Administration Building | Roof |  | rtu 1, 9.5 ton cooloing | n0k6950933 | York | dr120s20e4dzz30001d | 460 | [5 empty] | 3 |  | 192000 |  | Entech | 2016-04-21 |  | SORT-00000280
00000281 | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | D3050 : Terminal and Package Units | D305006 : ROOFTOP UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305006 : ROOFTOP UNIT | Alpha Ridge Administration Building | Roof |  | rtu 2, 9.5 ton cooloing | n0k6950932 | York | dr120s20e4dzz30001d | 460 | [5 empty] | 3 |  | 192000 |  | Entech | 2016-04-21 |  | SORT-00000281
00000876 | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | D3050 : Terminal and Package Units | D305006 : ROOFTOP UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305006 : ROOFTOP UNIT | Old West Friendship Firehouse | Roof |  |  | 4598G30071 | CARRIER | 48TJE008---521GA | [6 empty] | 3 |  | 180000 |  | Entech | 2016-05-11 |  | SORT-00000876
00000897 | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | D3050 : Terminal and Package Units | D305006 : ROOFTOP UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305006 : ROOFTOP UNIT | Scaggsville Public Safety Complex | Roof |  |  | 150940984 | diakin | dcc036xxx4bxxxac | [6 empty] | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000897
00000900 | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | D3050 : Terminal and Package Units | D305006 : ROOFTOP UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305006 : ROOFTOP UNIT | Scaggsville Public Safety Complex | Roof |  |  | 0611G10014 | Carrier | 50PG-C12-D-60-BP | [6 empty] | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000900
00000901 | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | D3050 : Terminal and Package Units | D305006 : ROOFTOP UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305006 : ROOFTOP UNIT | Scaggsville Public Safety Complex | Roof |  | mua-1 | 12336118 | greenheck | msx-100-h12-db | [10 empty] | Entech | 2016-05-17 |  | SORT-00000901
00001091 | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | D3050 : Terminal and Package Units | D305006 : ROOFTOP UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305006 : ROOFTOP UNIT | Florence Bain Senior Center | Roof |  | rtu-2 | 420101956L | Trane | yhc036a3ema1ed200a0a00300 | [6 empty] | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001091
00001092 | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | D3050 : Terminal and Package Units | D305006 : ROOFTOP UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305006 : ROOFTOP UNIT | Florence Bain Senior Center | Roof |  | rtu-1 | 4201001198L | Trane | yhc120a3ema1kd100a0a00300 | [6 empty] | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001092
00001093 | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | D3050 : Terminal and Package Units | D305006 : ROOFTOP UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305006 : ROOFTOP UNIT | Florence Bain Senior Center | Roof |  | rtu-1 | 420101836L | Trane | yhc036a3ema1ed200a0a00300 | [6 empty] | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001093
00001098 | RTU | Q,SA,A | UJPH-1239Q, UJPH-1239SA, UJPH-1239A | D3050 : Terminal and Package Units | D305006 : ROOFTOP UNIT | D3050 : TERMINAL AND PACKAGE UNITS | D305006 : ROOFTOP UNIT | Florence Bain Senior Center | Roof |  | #8153, tag florence bain | nehm71475 | York | y14an44c5cdaabb | 460 | [5 empty] | 3 |  | 372800 |  | Entech | 2016-05-19 |  | SORT-00001098
00000472 | TANK | A | UJPH-1073A | D2020 : Domestic Water Distribution | D202003 : STORAGE TANK - WATER | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : STORAGE TANK - WATER | Alpha Ridge Landfill - Pump Bldg | 1 - First Floor |  |  |  | reco penn | p2252 | [10 empty] | Entech | 2016-05-03 |  | SORT-00000472
00000571 | TANK | A | UJPH-1073A | D2020 : Domestic Water Distribution | D202003 : STORAGE TANK - WATER | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : STORAGE TANK - WATER | Western Regional Park - Concession | 0 - Ground Floor | 102 mechanical | 1000 gallon | [13 empty] | Entech | 2016-05-04 |  | SORT-00000571
00000572 | TANK | A | UJPH-1073A | D2020 : Domestic Water Distribution | D202003 : STORAGE TANK - WATER | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : STORAGE TANK - WATER | Western Regional Park - Concession | 0 - Ground Floor | 102 mechanical | 1000 gallon | [13 empty] | Entech | 2016-05-04 |  | SORT-00000572
00000617 | TANK | A | UJPH-1073A | D2020 : Domestic Water Distribution | D202003 : STORAGE TANK - WATER | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : STORAGE TANK - WATER | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | pump room | comfort station 1 | [13 empty] | Entech | 2016-05-04 |  | SORT-00000617
00000618 | TANK | A | UJPH-1073A | D2020 : Domestic Water Distribution | D202003 : STORAGE TANK - WATER | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : STORAGE TANK - WATER | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | pump room | comfort station 2 | [13 empty] | Entech | 2016-05-04 |  | SORT-00000618
00000646 | TANK | A | UJPH-1073A | D2020 : Domestic Water Distribution | D202003 : STORAGE TANK - WATER | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : STORAGE TANK - WATER | Western Regional Park - Maintenance Building | 0 - Ground Floor | mechanical | [14 empty] | Entech | 2016-05-05 |  | SORT-00000646
00000719 | TANK | A | UJPH-1073A | D2020 : Domestic Water Distribution | D202003 : STORAGE TANK - WATER | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : STORAGE TANK - WATER | Glenwood Community Center | 2 - Second Floor | mechanical | [14 empty] | Entech | 2016-05-05 |  | SORT-00000719
00000918 | TANK | A | UJPH-1073A | D2020 : Domestic Water Distribution | D202003 : STORAGE TANK - WATER | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : STORAGE TANK - WATER | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room |  | 55286 | westerman | [11 empty] | Entech | 2016-05-17 |  | SORT-00000918
00001079 | TANK | A | UJPH-1073A | D3090 : Other HVAC Systems and Equipment |  | D2020 : DOMESTIC WATER DISTRIBUTION | D202003 : STORAGE TANK - DOMESTIC WATER | Tubman Center - Grassroots | 0 - Basement | mechanical room | expansion tank domestic water | 168673 | Bell & Gossett | pta80v | [10 empty] | Entech | 2016-05-18 |  | SORT-00001079
00000440 | TANK | SA,A | UJPH-1077SA, UJPH-1077A | D3010 : Energy Supply | D301001 : STORAGE TANK - FUEL OIL | D3010 : ENERGY SUPPLY | D301001 : STORAGE TANK - FUEL OIL | Alpha Ridge Training Radio Facility | 1 - First Floor | generator room | 1500 gal, tank 001a |  | f | fireguard | [10 empty] | Entech | 2016-05-02 |  | SORT-00000440
00000488 | TANK | SA,A | UJPH-1077SA, UJPH-1077A | D3010 : Energy Supply | D301001 : STORAGE TANK - FUEL OIL | D3010 : ENERGY SUPPLY | D301001 : STORAGE TANK - FUEL OIL | Alpha Ridge Landfill - Shop | Exterior |  | 2000 gal #2 fuel oil |  | highland tank | [11 empty] | Entech | 2016-05-03 |  | SORT-00000488
00000536 | TANK | SA,A | UJPH-1077SA, UJPH-1077A | D3010 : Energy Supply | D301001 : STORAGE TANK - FUEL OIL | D3010 : ENERGY SUPPLY | D301001 : STORAGE TANK - FUEL OIL | Alpha Ridge Landfill - Truck Fill Building | Exterior |  | 275 gal, #2 fuel oil |  | simplex | [11 empty] | Entech | 2016-05-04 |  | SORT-00000536
00001134 | TANK | A | UJPH-1073A | D3090 : Other HVAC Systems and Equipment |  | D3020 : HEAT GENERATING SYSTEMS | D302002 : HOT WATER BOILERS - EXPANSION TANK | Florence Bain Senior Center | 0 - Ground Floor | mechanical | expansion tank | [13 empty] | Entech | 2016-05-19 |  | SORT-00001134
00001070 | TANK | A | UJPH-1073A | D3090 : Other HVAC Systems and Equipment |  | D3020 : HEAT GENERATING SYSTEMS | D302002 : HOT WATER BOILERS - EXPANSION TANK | Tubman Center - Grassroots | 0 - Basement | mechanical room | expansion tank condenser water, d280v | 168634 | Bell & Gossett | [11 empty] | Entech | 2016-05-18 |  | SORT-00001070
00001140 | UH | A | UJPH-1234A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - elec | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - ELECTRIC | Florence Bain Senior Center | 0 - Ground Floor | south vestibule | ceiling |  | Trane | vhca031a8a | 208 |  |  |  |  | 3 | 1 |  |  |  | Entech | 2016-05-19 |  | SORT-00001140
00001148 | UH | A | UJPH-1234A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - elec | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - ELECTRIC | Florence Bain Senior Center | 0 - Ground Floor | south west vestibule | ceiling | [13 empty] | Entech | 2016-05-19 |  | SORT-00001148
00000673 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Glenwood Library | 0 - Ground Floor | front hallway | hw cabinet heater |  | airtherm | [7 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000673
00000674 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Glenwood Library | 0 - Ground Floor | front hallway | hw cabinet heater |  | airtherm | [7 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000674
00000686 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Glenwood Library | 2 - Second Floor | mechanical mezzanine 1 |  | 8795106 | airtherm | hu-56 | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000686
00000692 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Glenwood Library | 2 - Second Floor | mechanical mezzanine 1 |  | 8795106 | airtherm | hu-55 | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000692
00000715 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Glenwood Library | 1 - First Floor | mechanical |  | 8795106 | airtherm | hu-55 | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000715
00000905 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Scaggsville Public Safety Complex | 0 - Ground Floor | sprinkler |  |  | durham-bush | durham-bush | [10 empty] | Entech | 2016-05-17 |  | SORT-00000905
00000954 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Scaggsville Public Safety Complex | 1 - First Floor | arson unit |  | 950150793 |  | h-175-c | 115 | [5 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000954
00000981 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Scaggsville Public Safety Complex | 0 - Ground Floor | vestibule | cabinet heater |  | durham bush | [11 empty] | Entech | 2016-05-18 |  | SORT-00000981
00000982 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Scaggsville Public Safety Complex | 0 - Ground Floor | mens locker room |  | 930750435 | durham bush | h-175-c | [6 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000982
00000994 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Scaggsville Public Safety Complex | 0 - Ground Floor | mens room |  |  |  |  | 115 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000994
00000995 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Scaggsville Public Safety Complex | 0 - Ground Floor | evidence storage room |  |  | durham bush | [7 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00000995
00001007 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room |  |  | durham bush |  | 115 | [9 empty] | Entech | 2016-05-18 |  | SORT-00001007
00001009 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Scaggsville Public Safety Complex | 0 - Ground Floor | fire station shop |  |  | durham bush | durham bush | [10 empty] | Entech | 2016-05-18 |  | SORT-00001009
00001010 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Scaggsville Public Safety Complex | 0 - Ground Floor | firestation vestibule | cabinet heater |  | international env corp |  | 115 | [5 empty] | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00001010
00001023 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Scaggsville Public Safety Complex | 0 - Ground Floor | office area |  |  | durham bush | [11 empty] | Entech | 2016-05-18 |  | SORT-00001023
00001025 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Scaggsville Public Safety Complex | 0 - Ground Floor | gear room |  | 930750431 | durham bush | h-175-0 | 115 | [9 empty] | Entech | 2016-05-18 |  | SORT-00001025
00001026 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Scaggsville Public Safety Complex | 0 - Ground Floor | sleep room | cabinet heater |  | international environmental | [11 empty] | Entech | 2016-05-18 |  | SORT-00001026
00001027 | UH | SA,A | UJPH-1135SA, UJPH-1135A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER - HW | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - HW | Scaggsville Public Safety Complex | 0 - Ground Floor | sleep room |  |  | durham bush | [11 empty] | Entech | 2016-05-18 |  | SORT-00001027
00001119 | UH | A | UJPH-1234A | D3020 : Heat Generating Systems | D302002 : UNIT HEATER -elec | D3020 : HEAT GENERATING SYSTEMS | D302002 : UNIT HEATER - ELECTRIC | Florence Bain Senior Center | 0 - Ground Floor | vestibule | in ceiling |  | Trane | uhca01a8a | 208 |  |  |  |  | 3 | 1 |  |  |  | Entech | 2016-05-19 |  | SORT-00001119
00000267 | UH | SA,A | UJPH-1233SA, UJPH-1233A | D3020 : Heat Generating Systems | D302004 : UNIT HEATER - GAS | D3020 : HEAT GENERATING SYSTEMS | D302004 : UNIT HEATER - GAS | Alpha Ridge Apparatus Storage Building | 1 - First Floor | main warehouse | uh-8 | bdi65m7l51997x | reznor | f100-e-3 | 115 | [5 empty] | 1 |  | 50000 |  | Entech | 2016-04-21 |  | SORT-00000267
00000345 | UH | SA,A | UJPH-1233SA, UJPH-1233A | D3020 : Heat Generating Systems | D302004 : UNIT HEATER - GAS | D3020 : HEAT GENERATING SYSTEMS | D302004 : UNIT HEATER - GAS | Alpha Ridge Apparatus Storage Building | 1 - First Floor |  | unit htr 5 | f100-e-3 | reznor | bdi65m7l51195x | 115 |  | 2.7 | 1/30 |  |  | 1 | 1050 | 80000 |  | Entech | 2016-04-22 |  | SORT-00000345
00000346 | UH | SA,A | UJPH-1233SA, UJPH-1233A | D3020 : Heat Generating Systems | D302004 : UNIT HEATER - GAS | D3020 : HEAT GENERATING SYSTEMS | D302004 : UNIT HEATER - GAS | Alpha Ridge Apparatus Storage Building | 1 - First Floor |  | unit htr 4 | f100-e-3 | reznor | bdi65m7l51190x | 115 |  | 2.7 | 1/30 |  |  | 1 | 1050 | 80000 |  | Entech | 2016-04-22 |  | SORT-00000346
00000347 | UH | SA,A | UJPH-1233SA, UJPH-1233A | D3020 : Heat Generating Systems | D302004 : UNIT HEATER - GAS | D3020 : HEAT GENERATING SYSTEMS | D302004 : UNIT HEATER - GAS | Alpha Ridge Apparatus Storage Building | 1 - First Floor |  | unit htr 3 | f100-e-3 | reznor | bdi65m7l51198x | 115 |  | 2.7 | 1/30 |  |  | 1 | 1050 | 80000 |  | Entech | 2016-04-22 |  | SORT-00000347
00000348 | UH | SA,A | UJPH-1233SA, UJPH-1233A | D3020 : Heat Generating Systems | D302004 : UNIT HEATER - GAS | D3020 : HEAT GENERATING SYSTEMS | D302004 : UNIT HEATER - GAS | Alpha Ridge Apparatus Storage Building | 1 - First Floor |  | unit htr 2 | f100-e-3 | reznor | bdi65m7l52000x | 115 |  | 2.7 | 1/30 |  |  | 1 | 1050 | 80000 |  | Entech | 2016-04-22 |  | SORT-00000348
00000349 | UH | SA,A | UJPH-1233SA, UJPH-1233A | D3020 : Heat Generating Systems | D302004 : UNIT HEATER - GAS | D3020 : HEAT GENERATING SYSTEMS | D302004 : UNIT HEATER - GAS | Alpha Ridge Apparatus Storage Building | 1 - First Floor |  | unit htr 1 | f100-e-3 | reznor | bdi65m7l51999x | 115 |  | 2.7 | 1/30 |  |  | 1 | 1050 | 80000 |  | Entech | 2016-04-22 |  | SORT-00000349
00000350 | UH | SA,A | UJPH-1233SA, UJPH-1233A | D3020 : Heat Generating Systems | D302004 : UNIT HEATER - GAS | D3020 : HEAT GENERATING SYSTEMS | D302004 : UNIT HEATER - GAS | Alpha Ridge Apparatus Storage Building | 1 - First Floor |  |  |  | reznor | v3t core | 115 |  | 2.7 | 1/30 |  |  | 1 | 1050 |  |  | Entech | 2016-04-22 |  | SORT-00000350
00000351 | UH | SA,A | UJPH-1233SA, UJPH-1233A | D3020 : Heat Generating Systems | D302004 : UNIT HEATER - GAS | D3020 : HEAT GENERATING SYSTEMS | D302004 : UNIT HEATER - GAS | Alpha Ridge Apparatus Storage Building | 1 - First Floor |  | unit htr 6 | f100-e-3 | reznor | bdi65m7l52001x | 115 |  | 2.7 | 1/30 |  |  | 1 | 1050 | 80000 |  | Entech | 2016-04-22 |  | SORT-00000351
00000638 | UH | SA,A | UJPH-1233SA, UJPH-1233A | D3020 : Heat Generating Systems | D302004 : UNIT HEATER - GAS | D3020 : HEAT GENERATING SYSTEMS | D302004 : UNIT HEATER - GAS | Western Regional Park - Maintenance Building | Exterior |  |  | 301011808-7480 | modine | tlp125h34 | [8 empty] | 100000 |  | Entech | 2016-05-05 |  | SORT-00000638
00000640 | UH | SA,A | UJPH-1233SA, UJPH-1233A | D3020 : Heat Generating Systems | D302004 : UNIT HEATER - GAS | D3020 : HEAT GENERATING SYSTEMS | D302004 : UNIT HEATER - GAS | Western Regional Park - Maintenance Building | 0 - Ground Floor |  |  | 3010118808-4782 | modine | tlp125h34 | [6 empty] | 1 |  | 100000 |  | Entech | 2016-05-05 |  | SORT-00000640
00000641 | UH | SA,A | UJPH-1233SA, UJPH-1233A | D3020 : Heat Generating Systems | D302004 : UNIT HEATER - GAS | D3020 : HEAT GENERATING SYSTEMS | D302004 : UNIT HEATER - GAS | Western Regional Park - Maintenance Building | 0 - Ground Floor |  |  | 3010118808-4783 | modine | tlp125h34 | [6 empty] | 1 |  | 100000 |  | Entech | 2016-05-05 |  | SORT-00000641
00000642 | UH | SA,A | UJPH-1233SA, UJPH-1233A | D3020 : Heat Generating Systems | D302004 : UNIT HEATER - GAS | D3020 : HEAT GENERATING SYSTEMS | D302004 : UNIT HEATER - GAS | Western Regional Park - Maintenance Building | 0 - Ground Floor |  |  | 3010118808-4781 | modine | tlp125h34 | [6 empty] | 1 |  | 100000 |  | Entech | 2016-05-05 |  | SORT-00000642
00000468 | FTH | A | UJPH-1094A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305004 : FIN TUBE RADIATION | Alpha Ridge Park - Comfort Station | 1 - First Floor | janitor pipe chase | finn tube |  | tpi | rph1-5a | [10 empty] | Entech | 2016-05-03 |  | SORT-00000468
00000569 | FTH | A | UJPH-1094A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305004 : FIN TUBE RADIATION | Western Regional Park - Concession | 0 - Ground Floor | 102 mechanical | finn tube baseboard |  | Trane | tr-dbf-4125-itd-ids | [7 empty] | 1 |  |  | Entech | 2016-05-04 |  | SORT-00000569
00000585 | FTH | A | UJPH-1094A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305004 : FIN TUBE RADIATION | Western Regional Park - Concession | 0 - Ground Floor | 101 rec office pipe chase | fin tube baseboard |  | Trane | tr-dbf-4125-itd-ids | [6 empty] | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000585
00000588 | FTH | A | UJPH-1094A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305004 : FIN TUBE RADIATION | Western Regional Park - Concession | 0 - Ground Floor | 109 storage area | fin tube |  | Dayton | 3ug82d | [6 empty] | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000588
00000629 | FTH | A | UJPH-1094A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305004 : FIN TUBE RADIATION | Western Regional Park - Comfort Station 2 | 0 - Ground Floor | janitor pipe chase | finn tube |  | marley | ht500 | [6 empty] | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000629
00000633 | FTH | A | UJPH-1094A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305004 : FIN TUBE RADIATION | Western Regional Park - Comfort Station 2 | 0 - Ground Floor | janitor | finn tube |  | marley | ht500 | [6 empty] | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000633
00000658 | FTH | A | UJPH-1094A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305004 : FIN TUBE RADIATION | Western Regional Park - Maintenance Building | 0 - Ground Floor | pipe chase | finn tube |  | tpi | e2005-d28s | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000658
00000832 | UH | A | UJPH-1234A | D3020 : Heat Generating Systems | D302099 : OTHER | D3020 : HEAT GENERATING SYSTEMS | D302099 : OTHER | Glenwood Fire Station No. 13 | Mezzanine |  | Duct Heater ITEM NO. 140-241333 |  | INDEECO |  |  |  | 27.76 |  |  | 10 | 3 |  |  |  | Entech | 2016-05-11 |  | SORT-00000832
00000845 | UH | A | UJPH-1140A | D3020 : Heat Generating Systems | D302099 : OTHER | D3020 : HEAT GENERATING SYSTEMS | D302099 : OTHER | Glenwood Fire Station No. 13 | 1 - First Floor |  | IRH-1 | 728452 | SPACE-RAY | PTS/U100-N5 |  |  | 1.74 |  |  |  | 1 |  | 100000 |  | Entech | 2016-05-11 |  | SORT-00000845
00000846 | UH | A | UJPH-1140A | D3020 : Heat Generating Systems | D302099 : OTHER | D3020 : HEAT GENERATING SYSTEMS | D302099 : OTHER | Glenwood Fire Station No. 13 | 1 - First Floor |  | IRH-1 | 728453 | SPACE -RAY | PTS/U 100-N5 |  |  | 1.74 |  |  |  | 1 |  | 100000 |  | Entech | 2016-05-11 |  | SORT-00000846
00000847 | UH | A | UJPH-1140A | D3020 : Heat Generating Systems | D302099 : OTHER | D3020 : HEAT GENERATING SYSTEMS | D302099 : OTHER | Glenwood Fire Station No. 13 | 1 - First Floor |  | IRH-1 | 728454 | SPACE-RAY | PTS/U 100-N5 |  |  | 1.74 |  |  |  | 1 |  | 100000 |  | Entech | 2016-05-11 |  | SORT-00000847
00000232 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Maze / Storage Building | 1 - First Floor |  | unit heater b |  | Dayton | 2yu61 | 208 |  | 0.25 |  |  | 3 | 1 |  |  |  | Entech | 2016-04-20 |  | SORT-00000232
00000233 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Maze / Storage Building | 1 - First Floor |  | unit heater a |  | Dayton | 2yu61 | 208 |  | 0.25 |  |  | 3 | 1 |  |  |  | Entech | 2016-04-20 |  | SORT-00000233
00000235 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Pump Building | 1 - First Floor |  | euh-5 | 1591292679 | qmark | muh0571 | 277 |  | 0.25 |  |  | 5 | 1 |  |  |  | Entech | 2016-04-20 |  | SORT-00000235
00000240 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Pump Building | 1 - First Floor |  | euh-4 | 1591292678 | qmark | muh0571 | 277 |  | 0.25 |  |  | 5 | 1 |  |  |  | Entech | 2016-04-20 |  | SORT-00000240
00000269 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Chemical Exposure Building | 1 - First Floor | bay a | unit heater 9 |  | qmark | muh0521 | 208/240 |  | 0.25 |  |  | 5 | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000269
00000272 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Chemical Exposure Building | 1 - First Floor | bay b | unit heater 10 |  | qmark | muh0521 | 208/240 |  | 0.25 |  |  | 5 | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000272
00000282 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Administration Building | 1 - First Floor | sprinkler shutoff room | ewh-3 |  | qmark | muh0341 | 480 |  | 0.15 |  |  | 3 | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000282
00000291 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Administration Building | 1 - First Floor | fire alarm annuciator room | euh-3 |  | qmark | muh0341 | 480 |  | 0.15 |  |  | 3 | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000291
00000298 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Administration Building | 1 - First Floor | main electrical room |  |  | qmark | muh0341 | 480 |  | 0.15 |  |  | 3 | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000298
00000305 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Hogans Alley Structure 3 | 1 - First Floor | main electrical room |  |  | Dayton | 2yu61 | 208 |  | 0.25 |  |  | 3 | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000305
00000343 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Fire Grounds Building | 1 - First Floor | 110 |  |  | Dayton | 2yu61 | 208 |  |  |  |  | 3 | 1 |  |  |  | Entech | 2016-04-22 |  | SORT-00000343
00000344 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Fire Grounds Building | 1 - First Floor |  |  |  | Dayton | 2yu61 | 208 |  |  |  |  | 3 | 1 |  |  |  | Entech | 2016-04-22 |  | SORT-00000344
00000450 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Simulation Training Building | 2 - Second Floor | mechanical room |  |  | qmark | muh0521 | [6 empty] | 5 | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000450
00000453 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Simulation Training Building | 2 - Second Floor | 210 mechanical room |  |  | qmark | muh0521 | [5 empty] | 5 | 3 |  |  |  | Entech | 2016-05-03 |  | SORT-00000453
00000459 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Simulation Training Building | 1 - First Floor | warehouse |  |  | qmark | muh0521 | [5 empty] | 5 | 3 |  |  |  | Entech | 2016-05-03 |  | SORT-00000459
00000461 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Park - Comfort Station | 1 - First Floor | mechanical |  |  | tpi | f3052t2dwb | [5 empty] | 2 |  |  |  |  | Entech | 2016-05-03 |  | SORT-00000461
00000462 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Park - Comfort Station | 1 - First Floor | storage |  |  | tpi | f3052t2dwb | [5 empty] | 2 |  |  |  |  | Entech | 2016-05-03 |  | SORT-00000462
00000463 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Park - Comfort Station | 1 - First Floor | storage |  |  | tpi | f3052t2dwb | [5 empty] | 2 |  |  |  |  | Entech | 2016-05-03 |  | SORT-00000463
00000464 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Park - Comfort Station | 1 - First Floor | womens room |  |  | tpi | f3327td-rp | [10 empty] | Entech | 2016-05-03 |  | SORT-00000464
00000465 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Park - Comfort Station | 1 - First Floor | mens room |  |  | tpi | f3327td-rp | [10 empty] | Entech | 2016-05-03 |  | SORT-00000465
00000467 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Park - Comfort Station | 1 - First Floor | janitor |  |  | tpi | f3052t2dwb | [5 empty] | 2 |  |  |  |  | Entech | 2016-05-03 |  | SORT-00000467
00000473 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Pump Bldg | 3 - Third Floor |  |  |  | qmark | muh0341 | [6 empty] | 3 | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000473
00000491 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Shop | 1 - First Floor | rain water harvest main control panel mcp-1 |  |  | tri | hf3215t2rpw | [10 empty] | Entech | 2016-05-03 |  | SORT-00000491
00000495 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Shop | 1 - First Floor | rain water harvest main control panel mcp-1 |  |  | tri | hf3215t2rpw | [10 empty] | Entech | 2016-05-03 |  | SORT-00000495
00000501 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Shop | 1 - First Floor | electrical room |  |  | marley | awh-4307-2-if | [6 empty] | 3 |  |  |  | Entech | 2016-05-03 |  | SORT-00000501
00000502 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Shop | 1 - First Floor | mens room |  |  | marley | awh-4207-1 | [6 empty] | 2 |  |  |  | Entech | 2016-05-03 |  | SORT-00000502
00000503 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Shop | 1 - First Floor | mens room |  |  | marley | whb3407fc | [6 empty] | 4 | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000503
00000530 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Truck Fill Building | 1 - First Floor |  |  |  | sentinel | 9120r | 480 | [5 empty] | 15 | 3 |  |  | Entech | 2016-05-04 |  | SORT-00000530
00000538 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Transfer Station Control Building | 1 - First Floor | spinkler |  |  | marley | cwh1208ds | 208 | [5 empty] | 2 |  |  |  | Entech | 2016-05-04 |  | SORT-00000538
00000544 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Transfer Station Control Building | 1 - First Floor | electrical room |  |  | marley | chw1208ds | 208 |  |  |  |  | 2 |  |  |  |  | Entech | 2016-05-04 |  | SORT-00000544
00000546 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Transfer Station Control Building | 0 - Ground Floor | fire alarm room |  |  | marley | cwh1208ds | 208 |  |  |  |  | 2 |  |  |  |  | Entech | 2016-05-04 |  | SORT-00000546
00000549 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Transfer Station Control Building | 0 - Ground Floor | restroom |  |  | marley | cwh1208ds | [5 empty] | 2 |  |  |  |  | Entech | 2016-05-04 |  | SORT-00000549
00000551 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Transfer Station Control Building | 0 - Ground Floor | restroom |  |  | marley | cwh1208ds | [5 empty] | 2 |  |  |  |  | Entech | 2016-05-04 |  | SORT-00000551
00000561 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Weigh Station | 0 - Ground Floor | restroom |  |  | emerson | fwh-ac-r2 | [5 empty] | 2 |  |  |  |  | Entech | 2016-05-04 |  | SORT-00000561
00000562 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Weigh Station | 0 - Ground Floor | hallway |  |  | marley | awh4307d | [5 empty] | 3 | 1 | 1 |  |  | Entech | 2016-05-04 |  | SORT-00000562
00000563 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Alpha Ridge Landfill - Weigh Station | 0 - Ground Floor | hallway |  |  | marley | wh4307 | [5 empty] | 3 | 1 | 1 |  |  | Entech | 2016-05-04 |  | SORT-00000563
00000568 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Western Regional Park - Concession | 0 - Ground Floor | mens room |  |  | Trane | uhaa021atad | [6 empty] | 2 | 1 |  |  | Entech | 2016-05-04 |  | SORT-00000568
00000570 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Western Regional Park - Concession | 0 - Ground Floor | 102 mechanical |  |  | Trane | uhaa021ata0 | [6 empty] | 2 | 1 |  |  | Entech | 2016-05-04 |  | SORT-00000570
00000582 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Western Regional Park - Concession | 0 - Ground Floor |  |  |  | Trane | uhaa021atad | [5 empty] | 2 | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000582
00000601 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Glenwood Library | Exterior | fire pump pit |  |  | marley | k304a | [5 empty] | 3 | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000601
00000624 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | womens room |  |  | marley | wh4508 | [6 empty] | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000624
00000625 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | mens room |  |  | marley | wh4508 | [6 empty] | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000625
00000634 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Western Regional Park - Comfort Station 2 | 0 - Ground Floor | mens room |  |  | marley | wh4508 | [6 empty] | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000634
00000635 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Western Regional Park - Comfort Station 2 | 0 - Ground Floor | womens room |  |  | marley | wh4508 | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000635
00000651 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Western Regional Park - Maintenance Building | 0 - Ground Floor | electrical |  |  | tpi | hf3325ttd-rp | [5 empty] | 3 | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000651
00000660 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Western Regional Park - Maintenance Building | 0 - Ground Floor | mens |  |  | tpi | hf3325ttd-rp | [5 empty] | 3 | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000660
00000661 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Western Regional Park - Maintenance Building | 0 - Ground Floor | womens |  |  | tpi | hf3325ttd-rp | [5 empty] | 3 | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000661
00000663 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Western Regional Park - Maintenance Pump Building | 0 - Ground Floor |  |  |  | tpi | hf1b5103n | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000663
00000667 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Western Regional Park - Maintenance Pump Building | 0 - Ground Floor |  |  |  | Dayton | 2yu65 | [5 empty] | 5 | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000667
00000678 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Glenwood Library | 2 - Second Floor | mechanical mezzanine 2 |  | 8795106 | aitherm | hu-55 | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000678
00000738 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Glenwood Community Center | 2 - Second Floor | mechanical |  |  | tpi | [6 empty] | 10 | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000738
00000747 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Glenwood Community Center | 1 - First Floor | sprinkler room |  |  | tpi | p3p5107ca1n | [6 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000747
00000775 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Glenwood Community Center | 1 - First Floor | mechanical room |  |  | tpi | p3p5107ca1n | [6 empty] | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000775
00000850 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Glenwood Fire Station No. 13 | 1 - First Floor | FIRE PUMP ROOM | ECR # 32745 | [8 empty] | 4 | 1 |  |  |  | Entech | 2016-05-11 |  | SORT-00000850
00000858 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : UNIT HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : UNIT HEATER - ELECTRIC | Glenwood Fire Station No. 13 | 1 - First Floor | MAINTENANCE SHOP |  |  | DAYTON | 2YU61 |  |  | 0.25 |  |  | 3 | 1 |  |  |  | Entech | 2016-05-11 |  | SORT-00000858
00000312 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305005 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305005 : UNIT HEATER - ELECTRIC | Alpha Ridge Kennel | 1 - First Floor | closet |  |  | fahrenheat | fuh series | [10 empty] | Entech | 2016-04-21 |  | SORT-00000312
00000313 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305005 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305005 : UNIT HEATER - ELECTRIC | Alpha Ridge Kennel | 1 - First Floor |  |  |  | qmark | muh0521 | 208/240 |  |  |  |  | 5 | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000313
00000319 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305005 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305005 : UNIT HEATER - ELECTRIC | Alpha Ridge Fire Grounds Building | 1 - First Floor | 113 |  |  | qmark | muh0521 | 208/240 |  |  |  |  | 5 | 3 |  |  |  | Entech | 2016-04-22 |  | SORT-00000319
00000323 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305005 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305005 : UNIT HEATER - ELECTRIC | Alpha Ridge Fire Grounds Building | 1 - First Floor | 108 |  |  | qmark | muh0521 | 208/240 |  |  |  |  | 5 | 3 |  |  |  | Entech | 2016-04-22 |  | SORT-00000323
00000339 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305005 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305005 : UNIT HEATER - ELECTRIC | Alpha Ridge Fire Grounds Building | 1 - First Floor | 112 |  |  | qmark | muh0521 | 208/240 |  |  |  |  | 5 | 3 |  |  |  | Entech | 2016-04-22 |  | SORT-00000339
00000675 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305005 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305005 : UNIT HEATER - ELECTRIC | Glenwood Library | 0 - Ground Floor | vestibule |  | 8795209 | airtherm | c60-475r1w45 | [6 empty] | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000675
00000821 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305005 : UNIT HEATER - ELECTRIC | D3050 : TERMINAL AND PACKAGE UNITS | D305005 : UNIT HEATER - ELECTRIC | Glenwood Community Center | 1 - First Floor | vestibule | [14 empty] | Entech | 2016-05-06 |  | SORT-00000821
00000396 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Alpha Ridge Administration Building | 1 - First Floor | west vestibule |  |  | Dayton | 5e187d | 277/240 |  |  |  |  | 4 | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000396
00000397 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Alpha Ridge Administration Building | 1 - First Floor | north vestibule |  |  | Dayton | 5e186d | 277/240 |  |  |  |  | 4 | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000397
00000398 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Alpha Ridge Administration Building | 1 - First Floor | ne vestibule |  |  | Dayton | 5e187d | 277/240 |  |  |  |  | 4 | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000398
00000399 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Alpha Ridge Administration Building | 1 - First Floor | north stairs |  |  | Dayton | 5e186d | 277/240 |  |  |  |  | 4 | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000399
00000400 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Alpha Ridge Administration Building | 1 - First Floor | north vestibule |  |  | Dayton | 5e187d | 277/240 |  |  |  |  | 4 | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000400
00000401 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Alpha Ridge Administration Building | 1 - First Floor | mens locker room | 173 |  | Dayton | 5e186d | 277/240 |  |  |  |  | 4 | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000401
00000402 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Alpha Ridge Administration Building | 1 - First Floor | mens locker room | 167 |  | Dayton | 5e186d | 277/240 |  |  |  |  | 4 | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000402
00000403 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Alpha Ridge Administration Building | 1 - First Floor | instructors locker room |  |  | Dayton | 5e186d | 277/240 |  |  |  |  | 4 | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000403
00000404 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Alpha Ridge Administration Building | 1 - First Floor | east vestibule |  |  | Dayton | 5e187d | 277/240 |  |  |  |  | 4 | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000404
00000444 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Alpha Ridge Simulation Training Building | 1 - First Floor | hall |  |  | marley | wh4408 | [5 empty] | 4 | 1 |  |  |  | Entech | 2016-05-03 |  | SORT-00000444
00000445 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Alpha Ridge Simulation Training Building | 1 - First Floor | 104 sprinkler room |  |  | marley | wh4408 | [5 empty] | 4 | 1 |  |  |  | Entech | 2016-05-03 |  | SORT-00000445
00000558 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Alpha Ridge Landfill - Weigh Station | 0 - Ground Floor | main |  |  | marley | wh4408 | [5 empty] | 4 | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000558
00000619 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | pump room |  |  | marley | wh4408 | [5 empty] | 4 | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000619
00000623 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | storage room |  |  | marley | wh4408 | [5 empty] | 4 | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000623
00000626 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | janitor |  |  | marley | wh4408 | [5 empty] | 4 | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000626
00000632 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305002 : WALL HEATER - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Western Regional Park - Comfort Station 2 | 0 - Ground Floor | janitor |  |  | marley | wh4408 | [5 empty] | 4 | 1 |  |  |  | Entech | 2016-05-04 |  | SORT-00000632
00000844 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305005: Wall Heater - ELEC | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Glenwood Fire Station No. 13 | 1 - First Floor |  |  |  | Marley | C1512T2B | 120 |  |  |  |  | 1.5 | 1 |  |  |  | Entech | 2016-05-11 |  | SORT-00000844
00000871 | UH | A | UJPH-1234A | D3020 : Heat Generating Systems | D302099 : OTHER | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Old West Friendship Firehouse | 2 - Second Floor |  | wall heater |  | MARLEY | AWH-4208-2-IF | [5 empty] | 2 |  |  |  |  | Entech | 2016-05-11 |  | SORT-00000871
00001087 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305005 : Wall Heater - Elec | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Tubman Center - Grassroots | 1 - First Floor | stairs | eh-2 |  | marley | wh4408 | 208 |  |  |  |  | 4 | 1 |  |  |  | Entech | 2016-05-16 |  | SORT-00001087
00001088 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305005 : Wall Heater - Elec | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Tubman Center - Grassroots | 2 - Second Floor | stairs | eh-4 |  | marley | wh4408 | 208 |  |  |  |  | 4 | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00001088
00001089 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305005 : Wall Heater - Elec | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Tubman Center - Grassroots | 2 - Second Floor | stairs | eh-5 |  | marley | wh4408 | 208 |  |  |  |  | 4 | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00001089
00001090 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305005 : Wall Heater - Elec | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Tubman Center - Grassroots | 1 - First Floor | mechanical stairs | eh-3 |  | marley | wh4408 | 208 |  |  |  |  | 4 | 1 |  |  |  | Entech | 2016-05-18 |  | SORT-00001090
00000741 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3050 : Terminal and Package Units | D305099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | police | cabinet heater | w14a00491 | Trane | gece00911b01a00001000b0021l000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000741
00000742 | HP | Q,A | UJPH-1059Q, UJPH-1059A | D3050 : Terminal and Package Units | D305099 : OTHER | D3030 : COOLING GENERATING SYSTEMS | D303002 : DIRECT EXPANSION SYSTEMS - HEAT PUMP | Glenwood Community Center | 1 - First Floor | police | cabinet heater | w15g19541 | Trane | gece01511c01000001100b10021l000000 | [6 empty] | 1 |  |  |  | Entech | 2016-05-06 |  | SORT-00000742
00000857 | UH | A | UJPH-1234A | D3050 : Terminal and Package Units | D305099 : OTHER | D3050 : TERMINAL AND PACKAGE UNITS | D305002 : WALL HEATER - ELECTRIC | Glenwood Fire Station No. 13 | 1 - First Floor | VESTIBULE | EH-1 |  | MARLEY | D500 |  |  | 4.2 |  |  |  | 1 |  |  |  | Entech | 2016-05-11 |  | SORT-00000857
00000437 | UPS | SA,A | UJPH-2086SA, UJPH-2086A | D5090: Other Electrical Services | D509002 : UPS | D5090 : OTHER ELECTRICAL SERVICES | D509002 : UPS | Alpha Ridge Training Radio Facility | 1 - First Floor |  |  | 650c120aaaaaaam | powerware | pw 9170 |  |  |  |  | 18 | 15 | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000437
00000955 | VAC | A | UGSA-HVAC-PMP-02-01Y | D3060 : Controls and Instrumentation | D306099 : OTHER | D3060 : CONTROLS AND INSTRUMENTATION | D306004 : INSTRUMENT AIR COMPRESSORS - VACUUM PUMP | Scaggsville Public Safety Complex | Exterior |  | vacuum pump | 5369 | american products | k552-750 | [6 empty] | 1 |  |  |  | Entech | 2016-05-17 |  | SORT-00000955
00000352 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | fire and rescue classrom 1 | 3-6 |  | metal aire | th512 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000352
00000353 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | emt classroom | 3-7 |  | metal aire | th514 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000353
00000354 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | fire and rescue classroom 2 | 3-3 |  | metal aire | th512 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000354
00000355 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | classroom a | 3-8 |  | metal aire | th510 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000355
00000356 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | classroom d | 3-15 |  | metal aire | th516 | 480 |  |  |  |  | 12 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000356
00000357 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | classroom d | 3-12 |  | metal aire | th506 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000357
00000358 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | classroom d | 3-11 |  | metal aire | th510 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000358
00000359 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | classroom a | 3-10 |  | metal aire | th510 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000359
00000360 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | classroom | 3-14 |  | metal aire | th508 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000360
00000365 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | computer room b | 5-09 |  | metal aire | th506 | 480 |  |  |  |  | 2 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000365
00000366 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | computer room b | 5-08 |  | metal aire | th512 | 480 | [9 empty] | Entech | 2016-05-02 |  | SORT-00000366
00000367 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | computer room b | 5-07 |  | metal aire | th506 | 480 |  |  |  |  | 2 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000367
00000368 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | police driver simulation | 5-11 |  | metal aire | th514 | 480 |  |  |  |  | 3 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000368
00000369 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | facilities | 5-12 |  | metal aire | th512 | 480 |  |  |  |  | 2 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000369
00000372 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | a\v closet | 5-10 |  | metal aire | th508 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000372
00000376 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | police classroom 2 | 5-13 |  | metal aire | th506 | 480 |  |  |  |  | 2 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000376
00000377 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | police classroom 2 | 5-05 |  | metal aire | th506 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000377
00000378 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | police classroom 2 | 5-06 |  | metal aire | th512 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000378
00000379 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | police classroom 2 | 5-04 |  | metal aire | th508 | 480 |  |  |  |  | 3 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000379
00000380 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | police classroom 2 | 5-03 |  | metal aire | th512 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000380
00000381 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | lunch room | 5-02 |  | metal aire | th514 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000381
00000382 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | lunch room | 5-01 |  | metal aire | th508 | 480 |  |  |  |  | 4 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000382
00000389 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | eleectrical room | 6-04 |  | metal aire | th508 | 480 |  |  |  |  | 3 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000389
00000390 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | electrical ROOM | 6-05 |  | metal aire | th516 | 480 |  |  |  |  | 12 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000390
00000392 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | gym | 6-06 |  | metal aire | th508 | 480 |  |  |  |  | 3 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000392
00000393 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | gym | 6-02 |  | metal aire | th516 | 480 |  |  |  |  | 10 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000393
00000394 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | gym | 6-01 |  | metal aire |  | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000394
00000395 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | fire learning resource center | 3-2 |  | metal aire | th512 | 480 |  |  |  |  | 8 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000395
00000406 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | break out room | 3-04 |  | metal aire | th506 | 480 |  |  |  |  | 2 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000406
00000407 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | break out room | 3-5 |  | metal aire | th508 | 480 |  |  |  |  | 3 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000407
00000408 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | classroom c | 3-1 |  | metal aire | th512 | 480 |  |  |  |  | 8 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000408
00000409 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 1 - First Floor | classroom c |  |  | metal aire | th510 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000409
00000410 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | reception | 4-01 |  | metal aire | th510 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000410
00000411 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | reception | 4-14 |  | metal aire | th516 | 480 |  |  |  |  | 12 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000411
00000412 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | reception | 4-13 |  | metal aire | th | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000412
00000413 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | reception |  |  | metal aire | th508 | 480 |  |  |  |  | 3 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000413
00000414 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | lt office | 4-02 |  | metal aire | th506 | 480 |  |  |  |  | 3 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000414
00000415 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | police files | 4-10 |  | metal aire | th510 | 480 |  |  |  |  | 4 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000415
00000416 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | corridor 227 | 4-11 |  | metal aire | th514 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000416
00000421 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | fire and rescue conference | 4-06 |  | metal aire | th506 | 480 |  |  |  |  | 3 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000421
00000422 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | corridor north | 4-07 |  | metal aire | th510 | 480 |  |  |  |  | 4 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000422
00000423 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | fire and rescue conference | 4-08 |  | metal aire | th512 | 480 |  |  |  |  | 5 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000423
00000424 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | fire and rescue office 4 | 4-05 |  | metal aire | th514 | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000424
00000425 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | fire and rescue office 4 | 4-15 |  | metal aire | th514 | 480 |  |  |  |  | 12 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000425
00000426 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | fire and rescue office 5 | 4-12 |  | metal aire | metal aire | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000426
00000427 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | fire and rescue office 5 | 4-12 |  | metal aire | metal aire | 480 | [5 empty] | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000427
00000441 | VAV | A | UJPH-1038A | D3040 : Distribution Systems | D304001 : VAV BOX W/ ELEC COIL | D3040 : DISTRIBUTION SYSTEMS | D304001 : VAV BOX W/ ELEC COIL | Alpha Ridge Administration Building | 2 - Second Floor | police conference room | 4-09 |  | metal aire | th510 | [5 empty] | 4 | 3 |  |  |  | Entech | 2016-05-02 |  | SORT-00000441
00000242 | VFD | A | UJPH-1036A | D5010 : Electrical Service and Distribution | D501007 : VARIABLE FREQUENCY DRIVE | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501007 : VARIABLE FREQUENCY DRIVE | Alpha Ridge Pump Building | 1 - First Floor |  |  | 2074602838 | allen bradley | [11 empty] | Entech | 2016-04-20 |  | SORT-00000242
00000648 | VFD | A | UJPH-1036A | D5010 : Electrical Service and Distribution | D501007 : VFD | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501007 : VARIABLE FREQUENCY DRIVE | Western Regional Park - Maintenance Building | 0 - Ground Floor | mechanical |  | 2114400953 | itt | aquavar | [6 empty] | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000648
00000717 | VFD | A | UJPH-1036A | D5010 : Electrical Service and Distribution | D501007 : VFD | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501007 : VARIABLE FREQUENCY DRIVE | Glenwood Community Center | 2 - Second Floor | mechanical | pump controller | 2152000723 | allen bradley | ACS550-U1-015A-4+N2000+X1555 | [6 empty] | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000717
00000733 | VFD | A | UJPH-1036A | D5010 : Electrical Service and Distribution | D501007 : VFD | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501007 : VARIABLE FREQUENCY DRIVE | Glenwood Community Center | 2 - Second Floor | mechanical |  |  | danfoss graham | vlt 6000 hvac | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000733
00000736 | VFD | A | UJPH-1036A | D5010 : Electrical Service and Distribution | D501007 : VFD | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501007 : VARIABLE FREQUENCY DRIVE | Glenwood Community Center | 2 - Second Floor | mechanical |  |  | danfoss graham | vlt 6000 hvac | [6 empty] | 1 |  |  |  | Entech | 2016-05-05 |  | SORT-00000736
00000924 | VFD | A | UJPH-1036A | D5010 : Electrical Service and Distribution | D501007 : VFD | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501007 : VARIABLE FREQUENCY DRIVE | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room |  | 2140602349 | allen bradley | ach550-vcr-038a4f267 | [10 empty] | Entech | 2016-05-17 |  | SORT-00000924
00000925 | VFD | A | UJPH-1036A | D5010 : Electrical Service and Distribution | D501007 : VFD | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501007 : VARIABLE FREQUENCY DRIVE | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room |  | 2153804939 | allen bradley | ach550-vcr-038a4f267 | [10 empty] | Entech | 2016-05-17 |  | SORT-00000925
00001059 | VFD | A | UJPH-1036A | D5010 : Electrical Service and Distribution | D501007 : VFD | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501007 : VARIABLE FREQUENCY DRIVE | Tubman Center - Grassroots | 0 - Basement | mechanical room |  | 12787301 | eaton |  | 208 |  |  | 7.5 |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001059
00001061 | VFD | A | UJPH-1036A | D5010 : Electrical Service and Distribution | D501007 : VFD | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501007 : VARIABLE FREQUENCY DRIVE | Tubman Center - Grassroots | 0 - Basement | mechanical room |  | 12787302 | eaton | hvx00711b1 | 208 |  |  | 7.5 |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001061
00001063 | VFD | A | UJPH-1036A | D5010 : Electrical Service and Distribution | D501007 : VFD | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501007 : VARIABLE FREQUENCY DRIVE | Tubman Center - Grassroots | 0 - Basement | mechanical room |  | 12787520 | eaton | hvx00711b1 | 208 |  |  | 7.5 |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001063
00001064 | VFD | A | UJPH-1036A | D5010 : Electrical Service and Distribution | D501007 : VFD | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501007 : VARIABLE FREQUENCY DRIVE | Tubman Center - Grassroots | 0 - Basement | mechanical room |  | 12787515 | eaton | hvx00711b1 | 208 |  |  | 7.5 |  |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001064
00000236 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Pump Building | 1 - First Floor |  | xfmr rpc | 42609 | poweresmiths | esaver-c3l-15-480-208 | 208/480 |  |  |  | 15 |  | 3 |  |  |  | Entech | 2016-04-20 |  | SORT-00000236 | Assuming this is a Dry Type
00000241 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Pump Building | 1 - First Floor |  |  |  | acme | t 1-81059 | 120/240 |  |  |  | 0.75 |  | 1 |  |  |  | Entech | 2016-04-20 |  | SORT-00000241 | Assuming this is a Dry Type
00000266 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Apparatus Storage Building | 1 - First Floor | main warehouse |  |  | acme | t279747s | 120/208/240/277 |  |  |  | 15 |  | 1 |  |  |  | Entech | 2016-04-21 |  | SORT-00000266 | Assuming this is a Dry Type
00000286 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Administration Building | 1 - First Floor | fire alarm annuciator room | xfmr erpa | 42612 | powersmiths | esaver-c3l-15-480-208 | 480 |  | 42 |  | 15 |  | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000286 | Assuming this is a Dry Type
00000297 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Administration Building | 1 - First Floor | main electrical room | xfmr swbb | 42613 | powersmiths | esaver-c3l-300-480-208 | 480 |  | 833 |  | 300 |  | 3 |  |  |  | Entech | 2016-04-21 |  | SORT-00000297 | Assuming this is a Dry Type
00000436 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Training Radio Facility | 1 - First Floor |  |  |  | Square-D | 5s1f | 480 |  |  |  | 5 |  | 1 |  |  |  | Entech | 2016-05-02 |  | SORT-00000436 | Assuming this is a Dry Type
00000471 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Landfill - Pump Bldg | 1 - First Floor |  |  |  | eaton | v48m28t15cueels42 | [5 empty] | 15 |  | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000471 | Assuming this is a Dry Type
00000474 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Landfill - Pump Bldg | 1 - First Floor |  |  |  | acme | t253013s |  |  |  |  | 3 |  |  | 1 |  |  | Entech | 2016-05-03 |  | SORT-00000474 | Assuming this is a Dry Type
00000478 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Landfill - Trailer | Exterior |  |  |  | Square-D | ee50s3h |  |  |  |  | 50 |  |  | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000478 | Assuming this is a Dry Type
00000487 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Landfill - Shop | Exterior |  | fed from panel d | 006500169152 | Square-D | ex30t6hct |  |  |  |  | 30 |  |  | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000487 | Assuming this is a Dry Type
00000498 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Landfill - Shop | 1 - First Floor | electrical room |  | 42605 | powersmiths | esaver-c3l-45-480-208 | 480 |  |  |  | 45 |  |  | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000498 | Assuming this is a Dry Type
00000522 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Landfill - Storage Building 2 | 0 - Ground Floor |  |  |  | Square-D | 15s1h | 480 |  |  |  |  | 15 |  | 3 |  |  | Entech | 2016-05-03 |  | SORT-00000522 | Assuming this is a Dry Type
00000532 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Landfill - Truck Fill Building | 1 - First Floor |  |  |  | Square-D | 6t2f | 480 |  |  |  |  | 6 |  | 3 |  |  | Entech | 2016-05-04 |  | SORT-00000532 | Assuming this is a Dry Type
00000545 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Landfill - Transfer Station Control Building | Exterior |  |  | 42608 | powersmiths | esaver-1ph-c3l-37.5-480-120/240 | 480 |  |  |  | 37.5 |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000545 | Assuming this is a Dry Type
00000565 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Alpha Ridge Landfill - Weigh Station | 0 - Ground Floor | electrical room |  |  | sorgel | t15t2f |  |  |  |  | 15 |  |  | 3 |  |  | Entech | 2016-05-04 |  | SORT-00000565 | Assuming this is a Dry Type
00000575 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Western Regional Park - Concession | 0 - Ground Floor | 108 electrical |  |  | Square-D | 45t3hcuee |  |  |  |  | 45 |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000575 | Assuming this is a Dry Type
00000596 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Glenwood Library | Exterior | fire pump pit |  |  | fedral pacific | se481d7.5f |  |  |  |  | 7.5 |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000596 | Assuming this is a Dry Type
00000622 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Western Regional Park - Comfort Station 1 | 0 - Ground Floor | electrical ROOM |  | j11a50323 | eaton | v48m28t45cuee |  |  |  |  | 45 |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000622 | Assuming this is a Dry Type
00000630 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Western Regional Park - Comfort Station 2 | 0 - Ground Floor | electrical |  | J11D50034A | eaton | v48m28t30cuee |  |  |  |  | 30 |  | 3 |  |  |  | Entech | 2016-05-04 |  | SORT-00000630 | Assuming this is a Dry Type
00000710 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Glenwood Library | 1 - First Floor | electrical | xfmr panel a | 42606 | powersmiths | esaver c3l-150-480-208 |  |  |  |  | 150 |  | 3 |  |  |  | Entech | 2016-05-05 |  | SORT-00000710 | Assuming this is a Dry Type
00000751 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Glenwood Community Center | 1 - First Floor | electrical c |  |  | eaton | v48m28t45ee |  |  |  |  | 45 |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000751 | Assuming this is a Dry Type
00000758 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Glenwood Community Center | 1 - First Floor | gym storage |  |  | eaton | v48m28t45ee |  |  |  |  | 45 |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000758 | Assuming this is a Dry Type
00000772 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Glenwood Community Center | 1 - First Floor | electrical room 155 |  | j05l05704 | eaton | v48u28t15ee |  |  |  |  | 15 |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000772 | Assuming this is a Dry Type
00000773 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Glenwood Community Center | 1 - First Floor | electrical room 155 |  | j05l05319 | eaton | v48u28t15ee |  |  |  |  | 15 |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000773 | Assuming this is a Dry Type
00000798 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Glenwood Community Center | 1 - First Floor | electrical closet 180 |  | j05l00737 | eaton | v48m28t12ee |  |  |  |  | 112.5 |  | 3 |  |  |  | Entech | 2016-05-06 |  | SORT-00000798 | Assuming this is a Dry Type
00000806 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Glenwood Community Center | 1 - First Floor | electrical 182 |  | j05l05771 | eaton | v48m28t75ee |  |  |  |  | 75 | [5 empty] | Entech | 2016-05-06 |  | SORT-00000806 | Assuming this is a Dry Type
00000842 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Glenwood Fire Station No. 13 | 1 - First Floor |  |  |  | General Electric | 9T21J9712 |  |  |  |  | 9 |  | 3 |  |  |  | Entech | 2016-05-11 |  | SORT-00000842 | Assuming this is a Dry Type
00000926 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Scaggsville Public Safety Complex | 0 - Ground Floor | mechanical room |  | 42684 | powersmiths | esaver c3l-75-480-208 | 480 |  |  |  | 75 |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000926 | Assuming this is a Dry Type
00000941 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | xfmr t1 | 42685 | powersmiths | esaver c3l-75-480-208 | 480 |  |  |  | 75 |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000941 | Assuming this is a Dry Type
00000942 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | xfmr t6 | 42682 | powersmiths | esaver c3l-45-480-208 | 480 |  |  |  | 45 |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000942 | Assuming this is a Dry Type
00000943 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | xfmr t5 | 42680 | powersmiths | esaver c3l-30-480-208 | 480 |  |  |  | 30 |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000943 | Assuming this is a Dry Type
00000944 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER | Scaggsville Public Safety Complex | 0 - Ground Floor | electrical 117 | xfmr t2 | 42683 | powersmiths | esaver c3l-45-480-208 | 480 |  |  |  | 45 |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000944 | Assuming this is a Dry Type
00000947 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER - SECONDARY | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER - SECONDARY | Scaggsville Public Safety Complex | 1 - First Floor | electrical room | xfmr t7 | 42679 | powersmiths | esaver-c3l-30-480-208 | 480 |  |  |  | 30 |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000947 | Assuming this is a Dry Type
00000948 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER - SECONDARY | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER - SECONDARY | Scaggsville Public Safety Complex | 1 - First Floor | electrical room | xfmr t8 | 42678 | powersmiths | esaver-c3l-30-480-208 | 480 |  |  |  | 30 |  | 3 |  |  |  | Entech | 2016-05-17 |  | SORT-00000948 | Assuming this is a Dry Type
00001011 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER - SECONDARY | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER - SECONDARY | Scaggsville Public Safety Complex | 0 - Ground Floor | firestation electrical room | xfmr t3 | 42607 | powersmiths | esaver-3cl-45-480-208 | 480 |  |  |  | 45 |  | 3 |  |  |  | Entech | 2016-05-18 |  | SORT-00001011 | Assuming this is a Dry Type
00001099 | XFMR | A | UJPH-1093A-D | D5010 : Electrical Service and Distribution | D501004 : TRANSFORMER - SECONDARY | D5010 : ELECTRICAL SERVICE AND DISTRIBUTION | D501004 : TRANSFORMER - SECONDARY | Florence Bain Senior Center | Roof |  |  |  | General Electric | 9t23b3875 | 480 |  |  |  | 112.5 |  | 3 |  |  |  | Entech | 2016-05-19 |  | SORT-00001099 | Assuming this is a Dry Type

## Job Plans
Asset Class | JPNUM | DESCRIPTION | SEQUENCE | JBT_DESCRIPTION
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 1 | SAFE WORK PRACTICES
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 2 | ___ Replace compressor oil
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 3 | ___ Perform operational check of compressed air system adjust as required
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 4 | ___ Check motor operation for excessive vibration, noise-overheating lubricate motor as required
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 5 | ___ Check operation of pressure relief valve
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 6 | ___ Clean cooling fans and air cooler on compressor, if equipped
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 7 | ___ Replace belts ensure proper tension Inspect sheaves ensure proper alignment
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 8 | ___ Check particle filter and oil and water filters; change if required
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 9 | ___ Drain tank and traps Check operation of auto-drain Test low-pressure cut in while draining
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 10 | ___ Clean or replace air intake filter
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 11 | ___ Check vibration dampers & flex hoses for wear
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 12 | ___ Clean dryer condenser and cover grills
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 13 | ___ Check dryer refrigerant pressure and temperature
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 14 | ___ Check and secure pipe & duct mounting hardware if applicable
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 15 | ___ Clean compressor and immediate area
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 16 | ___ Inspect tank and immediate piping for corrosion and leaks
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 17 | ___ Check pressure reducing valve settings
ACP | UJPH-1042A | ACP - Air Compressor - Annual | 18 | ___ Complete maintenance record and report deficiencies
ACP | UJPH-1042Q | ACP - Air Compressor - Quarterly | 1 | SAFE WORK PRACTICES
ACP | UJPH-1042Q | ACP - Air Compressor - Quarterly | 2 | ___ Check compressor oil level add as required
ACP | UJPH-1042Q | ACP - Air Compressor - Quarterly | 3 | ___ Perform operational check of compressed air system adjust as required
ACP | UJPH-1042Q | ACP - Air Compressor - Quarterly | 4 | ___ Check motor operation for excessive vibration, noise-overheating lubricate motor as required
ACP | UJPH-1042Q | ACP - Air Compressor - Quarterly | 5 | ___ Clean cooling fans and air cooler on compressor, if equipped
ACP | UJPH-1042Q | ACP - Air Compressor - Quarterly | 6 | ___ Visually inspect belts and sheaves for proper tension and alignment Adjust/replace as needed
ACP | UJPH-1042Q | ACP - Air Compressor - Quarterly | 7 | ___ Check particle filter and oil and water filters; change if required
ACP | UJPH-1042Q | ACP - Air Compressor - Quarterly | 8 | ___ Drain tank and traps Check operation of auto-drain Test low-pressure cut in while draining
ACP | UJPH-1042Q | ACP - Air Compressor - Quarterly | 9 | ___ Check air intake filter clean or replace if necessary
ACP | UJPH-1042Q | ACP - Air Compressor - Quarterly | 10 | ___ Check vibration dampers & flex hoses for wear
ACP | UJPH-1042Q | ACP - Air Compressor - Quarterly | 11 | ___ Check and secure pipe & duct mounting hardware if applicable
ACP | UJPH-1042Q | ACP - Air Compressor - Quarterly | 12 | ___ Clean compressor and immediate area
ACP | UJPH-1042Q | ACP - Air Compressor - Quarterly | 13 | ___ Check pressure reducing valve settings
ACP | UJPH-1042Q | ACP - Air Compressor - Quarterly | 14 | ___ Complete maintenance record and report deficiencies
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 1 | SAFE WORK PRACTICES
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 2 | ___ Check units operating condition Check with area personnel for deficiencies
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 3 | ___ Check operation of dampers and damper motors and lubricate as required
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 4 | ___ Clean coils, drip pan and blower assembly Inspect for damage and corrosion
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 5 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 6 | ___ Inspect motors for excessive noise and overheating, lube as required
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 7 | ___ Replace belts ensure proper tension Inspect sheaves ensure proper alignment
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 8 | ___ Grease blower shaft bearings
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 9 | ___ Inspect piping, compressor and valve for leaks tighten all loose connections as necessary
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 10 | ___ Check safeties and limits for proper operation
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 11 | ___ Test freeze protection, if applicable
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 12 | ___ Check compressor oil level, if applicable
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 13 | ___ Replace all disposable filters, clean reusable filters
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 14 | ___ Check and record refrigerant pressure _____________________________
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 15 | ___ Check sureness of guards, doors and panels Properly secure as required
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 16 | ___ Verify condensate drain system is operable
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 17 | ___ Clean area around unit
ACU | UJPH-1285A | ACU - Air Conditioning Unit - Annual | 18 | ___ Complete maintenance record and report deficiencies
ACU | UJPH-1285Q | ACU - Air Conditioning Unit - Quarterly | 1 | SAFE WORK PRACTICES
ACU | UJPH-1285Q | ACU - Air Conditioning Unit - Quarterly | 2 | ___ Check units operating condition Check with area personnel for deficiencies
ACU | UJPH-1285Q | ACU - Air Conditioning Unit - Quarterly | 3 | ___ Visually inspect filters if necessary, replace all disposable filters, clean reusable filters
ACU | UJPH-1285Q | ACU - Air Conditioning Unit - Quarterly | 4 | ___ Inspect piping, compressor and valve for leaks tighten all loose connections as necessary
ACU | UJPH-1285Q | ACU - Air Conditioning Unit - Quarterly | 5 | ___ Grease blower shaft bearings
ACU | UJPH-1285Q | ACU - Air Conditioning Unit - Quarterly | 6 | ___ Verify condensate drain system is operable
ACU | UJPH-1285Q | ACU - Air Conditioning Unit - Quarterly | 7 | ___ Test freeze protection, if applicable
ACU | UJPH-1285Q | ACU - Air Conditioning Unit - Quarterly | 8 | ___ Clean area around unit
ACU | UJPH-1285Q | ACU - Air Conditioning Unit - Quarterly | 9 | ___ Complete maintenance record and report deficiencies
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 1 | SAFE WORK PRACTICES
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 2 | ___ Replace all disposable filters, clean reusable filters
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 3 | NOTE: High efficiency and specialty filters (ie HEPA or Carbon) may not need replacement
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 4 | ___ Replace belts ensure proper tension Inspect sheaves ensure proper alignment
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 5 | ___ Visually check coils and piping for leaks
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 6 | ___ Verify condensate drain system is operable
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 7 | ___ Check motor operation for excessive vibration, noise-overheating lubricate motor as required
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 8 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 9 | ___ Clean fan assembly Inspect fan and shaft for proper alignment Lubricate bearing as required
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 10 | ___ Clean all coils straighten fins as required
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 11 | ___ Inspect coil piping and valves for leaks tighten all connections as required
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 12 | ___ Check for proper water flow, temperature, and pressures through the coil
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 13 | ___ Check and clean strainers, steam traps and hand valves
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 14 | ___ Clean and flush the waterside of water cooling/heating coils Verify proper flow through coils
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 15 | ___ Clean loose dirt and debris from interior and exterior of unit
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 16 | ___ Clean interior and external surfaces of the plenum chamber including dampers and louvers
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 17 | ___ Inspect plenum chamber, supply/return air ducts, branch ducts and mixing boxes
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 18 | ___ Check for damage to tie wires, binding bands, loose or broken connections, brackets and hangers
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 19 | ___ Verify all lights are working properly, replace bulbs or repair as necessary
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 20 | ___ Verify all covers and guards are secured No missing fasteners
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 21 | ___ Check for improper level of equipment, defective sound isolators and vibration absorbers
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 22 | ___ Check air handler for proper operation & discharge temperatures Adjust as required
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 23 | ___ Record Temps: Discharge: _______________ Return: ________________________
AHU | UJPH-1000A | AHU - Air Handling Unit - Annual | 24 | ___ Complete maintenance record and report deficiencies
AHU | UJPH-1000Q | AHU - Air Handling Unit - Quarterly | 1 | SAFE WORK PRACTICES
AHU | UJPH-1000Q | AHU - Air Handling Unit - Quarterly | 2 | ___ Check air handler for proper operation & discharge temperatures Adjust as required
AHU | UJPH-1000Q | AHU - Air Handling Unit - Quarterly | 3 | ___ Record Temps: Discharge: _______________ Return: ________________________
AHU | UJPH-1000Q | AHU - Air Handling Unit - Quarterly | 4 | ___ Visually inspect filters rotate roll filters if applicable Change filters if necessary
AHU | UJPH-1000Q | AHU - Air Handling Unit - Quarterly | 5 | ___ Visually inspect belts and sheaves for proper tension and alignment Change belts if necessary
AHU | UJPH-1000Q | AHU - Air Handling Unit - Quarterly | 6 | ___ Visually check coils and piping for leaks
AHU | UJPH-1000Q | AHU - Air Handling Unit - Quarterly | 7 | ___ Verify condensate drain system is operable
AHU | UJPH-1000Q | AHU - Air Handling Unit - Quarterly | 8 | ___ Check motor operation for excessive vibration, noise-overheating lubricate motor as required
AHU | UJPH-1000Q | AHU - Air Handling Unit - Quarterly | 9 | ___ Verify all lights are working properly, replace bulbs or repair as necessary
AHU | UJPH-1000Q | AHU - Air Handling Unit - Quarterly | 10 | ___ Verify all covers and guards are secured No missing fasteners
AHU | UJPH-1000Q | AHU - Air Handling Unit - Quarterly | 11 | ___ Complete maintenance record and report deficiencies
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 1 | SAFE WORK PRACTICES
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 2 | ___ Replace all disposable filters, clean reusable filters
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 3 | NOTE: High efficiency and specialty filters (ie HEPA or Carbon) may not need replacement
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 4 | ___ Visually inspect belts and sheaves for proper tension and alignment Adjust/replace as needed
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 5 | ___ Visually check coils and piping for leaks
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 6 | ___ Verify condensate drain system is operable
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 7 | ___ Check motor operation for excessive vibration, noise-overheating lubricate motor as required
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 8 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 9 | ___ Clean fan assembly Inspect fan and shaft for proper alignment Lubricate bearing as required
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 10 | ___ Inspect coil piping and valves for leaks tighten all connections as required
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 11 | ___ Check for proper water flow, temperature, and pressures through the coil
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 12 | ___ Check and clean strainers, steam traps and hand valves
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 13 | ___ Clean and flush the waterside of water cooling/heating coils Verify proper flow through coils
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 14 | ___ Clean loose dirt and debris from interior and exterior of unit
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 15 | ___ Verify all lights are working properly, replace bulbs or repair as necessary
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 16 | ___ Verify all covers and guards are secured No missing fasteners
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 17 | ___ Check air handler for proper operation & discharge temperatures Adjust as required
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 18 | ___ Record Temps: Discharge: _______________ Return: ________________________
AHU | UJPH-1000SA | AHU - Air Handling Unit - Semi-Annual | 19 | ___ Complete maintenance record and report deficiencies
ATS | UJPH-1171A | ATS - Automatic Transfer Switch - Annual | 1 | SAFE WORK PRACTICES
ATS | UJPH-1171A | ATS - Automatic Transfer Switch - Annual | 2 | ___ Check with area personnel for deficiencies
ATS | UJPH-1171A | ATS - Automatic Transfer Switch - Annual | 3 | ___ Visually check wires, connections, fuseblocks for looseness, charring, shorts, overheating
ATS | UJPH-1171A | ATS - Automatic Transfer Switch - Annual | 4 | ___ If applicable, check all lights replace bulbs if necessary
ATS | UJPH-1171A | ATS - Automatic Transfer Switch - Annual | 5 | ___ Test all fuses
ATS | UJPH-1171A | ATS - Automatic Transfer Switch - Annual | 6 | ___ Inspect general condition of switch and clean exterior and surrounding area
ATS | UJPH-1171A | ATS - Automatic Transfer Switch - Annual | 7 | ___ Complete maintenance record and report deficiencies
BAS | UJPH-1109A | BAS - Building Automation System - Annual | 1 | SAFE WORK PRACTICES
BAS | UJPH-1109A | BAS - Building Automation System - Annual | 2 | ___ SCU Frontend - Visually inspect SCU and observe operational functions.
BAS | UJPH-1109A | BAS - Building Automation System - Annual | 3 | ___ SCU Frontend - Check clock, reset or update for Day-Light-Savings as required.
BAS | UJPH-1109A | BAS - Building Automation System - Annual | 4 | ___ SCU Frontend - Review all active alarms and print alarm log.
BAS | UJPH-1109A | BAS - Building Automation System - Annual | 5 | ___ SCU Frontend - After printing report, clear all alarms and submit alarm log to the supervisor.
BAS | UJPH-1109A | BAS - Building Automation System - Annual | 6 | ___ Complete maintenance record and report deficiencies
BOILER | UJPH-1144A | BLR - Boiler - Annual | 1 | SAFE WORK PRACTICES
BOILER | UJPH-1144A | BLR - Boiler - Annual | 2 | ___ Internal inspection of boiler
BOILER | UJPH-1144A | BLR - Boiler - Annual | 3 | ___ Cleaning of boiler (external parts)
BOILER | UJPH-1144A | BLR - Boiler - Annual | 4 | ___ Control panel inspection
BOILER | UJPH-1144A | BLR - Boiler - Annual | 5 | ___ Gasket Inspection
BOILER | UJPH-1144A | BLR - Boiler - Annual | 6 | ___ Low water cut-off control check
BOILER | UJPH-1144A | BLR - Boiler - Annual | 7 | ___ Water gauge glass inspection
BOILER | UJPH-1144A | BLR - Boiler - Annual | 8 | ___ Fire side (interior) cleaning, as needed
BOILER | UJPH-1144A | BLR - Boiler - Annual | 9 | ___ Water side (interior) cleaning
BOILER | UJPH-1144A | BLR - Boiler - Annual | 10 | ___ Safety valve inspection/cleaning
BOILER | UJPH-1144A | BLR - Boiler - Annual | 11 | ___ Fire rate control check
BOILER | UJPH-1144A | BLR - Boiler - Annual | 12 | ___ Fuel/vent/stack outlet inspection
BOILER | UJPH-1144A | BLR - Boiler - Annual | 13 | ___ Combustion air inspection
BOILER | UJPH-1144A | BLR - Boiler - Annual | 14 | ___ Ignition Systems Inspection
BOILER | UJPH-1144A | BLR - Boiler - Annual | 15 | ___ Pilot fuel Valve inspection
BOILER | UJPH-1144A | BLR - Boiler - Annual | 16 | ___ Combustion safety control check
BOILER | UJPH-1144A | BLR - Boiler - Annual | 17 | ___ High limit safety control check
BOILER | UJPH-1144A | BLR - Boiler - Annual | 18 | ___ Operating control check
BOILER | UJPH-1144A | BLR - Boiler - Annual | 19 | ___ Low draft, fan, air press and damper check
BOILER | UJPH-1144A | BLR - Boiler - Annual | 20 | ___ High/Low gas pressure interlock check
BOILER | UJPH-1144A | BLR - Boiler - Annual | 21 | ___ Low oil interlock check
BOILER | UJPH-1144A | BLR - Boiler - Annual | 22 | ___ Fuel valve interlock check
BOILER | UJPH-1144A | BLR - Boiler - Annual | 23 | ___ Purge switch check
BOILER | UJPH-1144A | BLR - Boiler - Annual | 24 | ___ Low fire start interlock check
BOILER | UJPH-1144A | BLR - Boiler - Annual | 25 | ___ Auto changeover control check
BOILER | UJPH-1144A | BLR - Boiler - Annual | 26 | ___ Inspect burner components
BOILER | UJPH-1144A | BLR - Boiler - Annual | 27 | ___ Remove oil drawer assembly
BOILER | UJPH-1144A | BLR - Boiler - Annual | 28 | ___ Clean blower motor/blower wheel
BOILER | UJPH-1144A | BLR - Boiler - Annual | 29 | ___ Remove/clean gas pilot assembly
BOILER | UJPH-1144A | BLR - Boiler - Annual | 30 | ___ Complete maintenance record and report deficiencies
BOILER | UJPH-1144AIC | BLR - Boiler Inspection & Certification - Annual | 1 | SAFE WORK PRACTICES
BOILER | UJPH-1144AIC | BLR - Boiler Inspection & Certification - Annual | 2 | ___ Perform certification of boiler Third party Certification
BOILER | UJPH-1144AIC | BLR - Boiler Inspection & Certification - Annual | 3 | ___ Complete maintenance record and report deficiencies
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 1 | SAFE WORK PRACTICES
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 2 | ___ Cleaning of boiler (external parts)
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 3 | ___ Control panel inspection
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 4 | ___ Gasket Inspection
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 5 | ___ Low water cut-off control check
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 6 | ___ Water gauge glass inspection
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 7 | ___ Safety valve inspection/cleaning
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 8 | ___ Fire rate control check
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 9 | ___ Fuel/vent/stack outlet inspection
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 10 | ___ Combustion air inspection
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 11 | ___ Ignition Systems Inspection
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 12 | ___ Pilot fuel Valve inspection
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 13 | ___ Combustion safety control check
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 14 | ___ Low draft, fan, air press and damper check
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 15 | ___ High/Low gas pressure interlock check
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 16 | ___ Low oil interlock check
BOILER | UJPH-1144Q | BLR - Boiler - Quarterly | 17 | ___ Complete maintenance record and report deficiencies
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 1 | SAFE WORK PRACTICES
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 2 | ___ Is Chiller Running? Yes ____ No ____
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 3 | ___ Check unit for proper operation, excessive noise or vibration
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 4 | ___ Record Temps: Supply ____________ Return ____________ Oil ____________
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 5 | ___ Run system controls/diagnostics tests Record Error Messages and/or Codes
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 6 | ___ Check operating hours, starts and meg readings of all motors and record
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 7 | ___ Check-Adjust controls, limits and safeties Ensure all interlock equipment is operating
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 8 | ___ Check oil level in sight glass of compressor
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 9 | ___ Perform spectrochemical analysis of compressor oil Replace oil filter add oil as necessary
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 10 | ___ Check liquid line sight glass
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 11 | ___ Install gauges check for correct operating pressures Check pump down cycle and adjust
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 12 | ___ Replace belts ensure proper tension Inspect sheaves ensure proper alignment
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 13 | ___ Clean all coils
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 14 | ___ Inspect condenser fans for operation
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 15 | ___ Check contactors, sensors and mechanical safety limits Clean and adjust as necessary
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 16 | ___ Check electrical wiring and connections tighten loose connections
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 17 | ___ Check operation of switch gear/starter/contacts Check motor overloads (heaters) for wear
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 18 | ___ Check evaporator and condenser for corrosion
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 19 | ___ Lubricate shaft bearings and motor bearings as required
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 20 | ___ Inspect machine exterior, piping and structure elements for corrosion, rust and leaks
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 21 | ___ Record superheat and sub cooling temperatures:
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 22 | ___ Perform leak check on refrigeration system Check capillary tubes for wear, damage and leaks
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 23 | ___ Check sureness of guards, doors, and panels Properly secure as required
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 24 | ___ Clean chiller and surrounding area
CHILLER | UJPH-1052A | Chiller Air Cooled - Annual | 25 | ___ Complete maintenance record and report deficiencies
CHILLER | UJPH-1052M | Chiller Air Cooled - Monthly | 1 | SAFE WORK PRACTICES
CHILLER | UJPH-1052M | Chiller Air Cooled - Monthly | 2 | ___ Is Chiller Running? Yes ____ No ____
CHILLER | UJPH-1052M | Chiller Air Cooled - Monthly | 3 | ___ Check unit for proper operation, excessive noise or vibration
CHILLER | UJPH-1052M | Chiller Air Cooled - Monthly | 4 | ___ Record Temps: Supply ____________ Return ____________ Oil ____________
CHILLER | UJPH-1052M | Chiller Air Cooled - Monthly | 5 | ___ Run system controls/diagnostics tests Record Error Messages and/or Codes
CHILLER | UJPH-1052M | Chiller Air Cooled - Monthly | 6 | ___ Check oil level in sight glass of compressor
CHILLER | UJPH-1052M | Chiller Air Cooled - Monthly | 7 | ___ Check liquid line sight glass
CHILLER | UJPH-1052M | Chiller Air Cooled - Monthly | 8 | ___ Visually inspect belts and sheaves for proper tension and alignment Adjust/replace as needed
CHILLER | UJPH-1052M | Chiller Air Cooled - Monthly | 9 | ___ Check sureness of guards, doors, and panels Properly secure as required
CHILLER | UJPH-1052M | Chiller Air Cooled - Monthly | 10 | ___ Complete maintenance record and report deficiencies
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 1 | SAFE WORK PRACTICES
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 2 | ___ Is Chiller Running? Yes ____ No ____
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 3 | ___ Check unit for proper operation, excessive noise or vibration
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 4 | ___ Record Temps: Supply ____________ Return ____________ Oil ____________
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 5 | ___ Run system controls/diagnostics tests Record Error Messages and/or Codes
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 6 | ___ Check oil level in sight glass of compressor
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 7 | ___ Check liquid line sight glass
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 8 | ___ Visually inspect belts and sheaves for proper tension and alignment Adjust/replace as needed
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 9 | ___ Clear intake side of condenser coil, fans and intake screens
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 10 | ___ Clean condenser coils
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 11 | ___ Inspect condenser fans for operation
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 12 | ___ Check evaporator and condenser for corrosion
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 13 | ___ Lubricate shaft bearings and motor bearings as required
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 14 | ___ Check sureness of guards, doors, and panels Properly secure as required
CHILLER | UJPH-1052Q | Chiller Air Cooled - Quarterly | 15 | ___ Complete maintenance record and report deficiencies
COND | UJPH-1063A | COND - Condenser - Annual | 1 | SAFE WORK PRACTICES
COND | UJPH-1063A | COND - Condenser - Annual | 2 | ___ Check units operating condition Check with area personnel for deficiencies
COND | UJPH-1063A | COND - Condenser - Annual | 3 | ___ Clean condenser coils, fans and intake screens& straighten fins
COND | UJPH-1063A | COND - Condenser - Annual | 4 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
COND | UJPH-1063A | COND - Condenser - Annual | 5 | ___ Inspect motors for excessive noise and overheating, lube as required
COND | UJPH-1063A | COND - Condenser - Annual | 6 | ___ Inspect piping, compressor and valve for leaks tighten all loose connections as necessary
COND | UJPH-1063A | COND - Condenser - Annual | 7 | ___ Check safeties and limits for proper operation
COND | UJPH-1063A | COND - Condenser - Annual | 8 | ___ On direct expansion systems, check for frosting or icing of coil
COND | UJPH-1063A | COND - Condenser - Annual | 9 | ___ Check and record refrigerant pressure _____________________________
COND | UJPH-1063A | COND - Condenser - Annual | 10 | ___ Complete maintenance record and report deficiencies
COND | UJPH-1063Q | COND - Condenser - Quarterly | 1 | SAFE WORK PRACTICES
COND | UJPH-1063Q | COND - Condenser - Quarterly | 2 | ___ Check units operating condition Check with area personnel for deficiencies
COND | UJPH-1063Q | COND - Condenser - Quarterly | 3 | ___ Check operation of dampers and damper motors
COND | UJPH-1063Q | COND - Condenser - Quarterly | 4 | ___ Clean condenser coils and intake screens
COND | UJPH-1063Q | COND - Condenser - Quarterly | 5 | ___ Inspect motors for excessive noise and overheating, lube as required
COND | UJPH-1063Q | COND - Condenser - Quarterly | 6 | ___ Visually inspect belts and sheaves for proper tension and alignment Adjust/replace as needed
COND | UJPH-1063Q | COND - Condenser - Quarterly | 7 | ___ Inspect piping, compressor and valve for leaks tighten all loose connections as necessary
COND | UJPH-1063Q | COND - Condenser - Quarterly | 8 | ___ On direct expansion systems, check for frosting or icing of coil
COND | UJPH-1063Q | COND - Condenser - Quarterly | 9 | ___ Verify condensate drain system is operable
COND | UJPH-1063Q | COND - Condenser - Quarterly | 10 | ___ Complete maintenance record and report deficiencies
CONTROLLER | UJPH-1002A | CONTROL - Control Panel - Annual | 1 | SAFE WORK PRACTICES
CONTROLLER | UJPH-1002A | CONTROL - Control Panel - Annual | 2 | ___ Check with operating or area personnel for deficiencies
CONTROLLER | UJPH-1002A | CONTROL - Control Panel - Annual | 3 | ___ Check for excessive heat, odors, noise, charring and vibration
CONTROLLER | UJPH-1002A | CONTROL - Control Panel - Annual | 4 | ___ Run self-check or diagnostics if applicable and record error codes
CONTROLLER | UJPH-1002A | CONTROL - Control Panel - Annual | 5 | ___ Check fuses, breakers and-or disconnects if applicable
CONTROLLER | UJPH-1002A | CONTROL - Control Panel - Annual | 6 | ___ Clean and check general condition of panel
CONTROLLER | UJPH-1002A | CONTROL - Control Panel - Annual | 7 | ___ Complete maintenance record and report deficiencies
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 1 | SAFE WORK PRACTICES
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 2 | ___ Check with operating personnel for deficiencies
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 3 | ___ Run microprocessor check, if available, or check controls and unit for proper operation
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 4 | ___ Check for unusual noise and vibration
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 5 | ___ Clean coils, evaporator drain pan, humidifier drain pan, blower, motor and draining piping
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 6 | ___ Verify condensate drain system is operable
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 7 | ___ Replace all disposable filters, clean reusable filters
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 8 | ___ Lubricate shaft and motor bearing
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 9 | ___ Replace belts ensure proper tension Inspect sheaves ensure proper alignment
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 10 | ___ Check humidity lamp, replace as required
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 11 | ___ Check and clean humidity canister, heating element and valve
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 12 | ___ Inspect exterior piping and valves for leaks tighten connections as required
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 13 | ___ During operation of unit, check & record refrigerant pressures _________________________
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 14 | ___ Check CRU for proper operation & discharge temperatures Adjust as required
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 15 | ___ Record Temps: Discharge: _______________
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 16 | ___ Verify all covers and guards are secured No missing fasteners
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 17 | ___ Clean around unit
CRAC | UJPH-1013A | CRU - Computer Room Unit - Annual | 18 | ___ Complete maintenance record and report deficiencies
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 1 | SAFE WORK PRACTICES
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 2 | ___ Check with operating personnel for deficiencies
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 3 | ___ Run microprocessor check, if available, or check controls and unit for proper operation
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 4 | ___ Check for unusual noise and vibration
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 5 | ___ Verify condensate drain system is operable
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 6 | ___ Replace all disposable filters, clean reusable filters
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 7 | ___ Lubricate shaft and motor bearing
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 8 | ___ Visually inspect belts and sheaves for proper tension and alignment Adjust/replace as needed
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 9 | ___ Check humidity lamp, replace as required
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 10 | ___ Inspect exterior piping and valves for leaks tighten connections as required
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 11 | ___ Check CRU for proper operation & discharge temperatures Adjust as required
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 12 | ___ Record Temps: Discharge: _______________
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 13 | ___ Verify all covers and guards are secured No missing fasteners
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 14 | ___ Clean around unit
CRAC | UJPH-1013Q | CRU - Computer Room Unit - Quarterly | 15 | ___ Complete maintenance record and report deficiencies
CRAC | UJPH-1013SA | CRU - Computer Room Unit - Semi-Annual | 1 | SAFE WORK PRACTICES
CRAC | UJPH-1013SA | CRU - Computer Room Unit - Semi-Annual | 2 | ___ Check with operating personnel for deficiencies
CRAC | UJPH-1013SA | CRU - Computer Room Unit - Semi-Annual | 3 | ___ Run microprocessor check, if available, or check controls and unit for proper operation
CRAC | UJPH-1013SA | CRU - Computer Room Unit - Semi-Annual | 4 | ___ Check for unusual noise and vibration
CRAC | UJPH-1013SA | CRU - Computer Room Unit - Semi-Annual | 5 | ___ Verify condensate drain system is operable
CRAC | UJPH-1013SA | CRU - Computer Room Unit - Semi-Annual | 6 | ___ Replace all disposable filters, clean reusable filters
CRAC | UJPH-1013SA | CRU - Computer Room Unit - Semi-Annual | 7 | ___ Lubricate shaft and motor bearing
CRAC | UJPH-1013SA | CRU - Computer Room Unit - Semi-Annual | 8 | ___ Visually inspect belts and sheaves for proper tension and alignment Adjust/replace as needed
CRAC | UJPH-1013SA | CRU - Computer Room Unit - Semi-Annual | 9 | ___ Inspect exterior piping and valves for leaks tighten connections as required
CRAC | UJPH-1013SA | CRU - Computer Room Unit - Semi-Annual | 10 | ___ Check CRU for proper operation & discharge temperatures Adjust as required
CRAC | UJPH-1013SA | CRU - Computer Room Unit - Semi-Annual | 11 | ___ Record Temps: Discharge: _______________
CRAC | UJPH-1013SA | CRU - Computer Room Unit - Semi-Annual | 12 | ___ Verify all covers and guards are secured No missing fasteners
CRAC | UJPH-1013SA | CRU - Computer Room Unit - Semi-Annual | 13 | ___ Clean around unit
CRAC | UJPH-1013SA | CRU - Computer Room Unit - Semi-Annual | 14 | ___ Complete maintenance record and report deficiencies
CT | UJPH-1005A | CT - Cooling Tower - Annual | 1 | SAFE WORK PRACTICES
CT | UJPH-1005A | CT - Cooling Tower - Annual | 2 | ___ Check operation of unit for water leaks, noise and vibrations
CT | UJPH-1005A | CT - Cooling Tower - Annual | 3 | ___ Clean and inspect hot water basin
CT | UJPH-1005A | CT - Cooling Tower - Annual | 4 | ___ Inspect motors for excessive noise and overheating, lube as required
CT | UJPH-1005A | CT - Cooling Tower - Annual | 5 | ___ Visually inspect belts and sheaves for proper tension and alignment Adjust/replace as needed
CT | UJPH-1005A | CT - Cooling Tower - Annual | 6 | ___ Inspect blower wheels and fan blades for bent or unbalanced blades and tip clearance
CT | UJPH-1005A | CT - Cooling Tower - Annual | 7 | ___ Lubricate fan shaft bearings
CT | UJPH-1005A | CT - Cooling Tower - Annual | 8 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
CT | UJPH-1005A | CT - Cooling Tower - Annual | 9 | ___ Inspect contactors relays operating safety controls and pan heaters
CT | UJPH-1005A | CT - Cooling Tower - Annual | 10 | ___ Drain and back flush cold-water sump and clean strainers
CT | UJPH-1005A | CT - Cooling Tower - Annual | 11 | ___ Clean inside of water tower using water hose scrape, brush and wipe as required
CT | UJPH-1005A | CT - Cooling Tower - Annual | 12 | ___ Check and clean spray nozzles
CT | UJPH-1005A | CT - Cooling Tower - Annual | 13 | ___ Inspect and clean float assembly bleed overflow and drain for proper operation
CT | UJPH-1005A | CT - Cooling Tower - Annual | 14 | ___ Inspect piping and valves for leaks tighten as required
CT | UJPH-1005A | CT - Cooling Tower - Annual | 15 | ___ Check damper motors and butterfly valves for proper operation Adjustment as required
CT | UJPH-1005A | CT - Cooling Tower - Annual | 16 | ___ Perform operational check adjust controls as required
CT | UJPH-1005A | CT - Cooling Tower - Annual | 17 | ___ Remove all debris from within and around unit
CT | UJPH-1005A | CT - Cooling Tower - Annual | 18 | ___ Complete maintenance record and report deficiencies
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 1 | SAFE WORK PRACTICES
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 2 | ___ Check operation of unit for water leaks, noise and vibrations
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 3 | ___ Clean and inspect hot water basin
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 4 | ___ Inspect motors for excessive noise and overheating, lube as required
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 5 | ___ Visually inspect belts and sheaves for proper tension and alignment Adjust/replace as needed
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 6 | ___ Inspect blower wheels and fan blades for bent or unbalanced blades and tip clearance
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 7 | ___ Lubricate fan shaft bearings
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 8 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 9 | ___ Inspect contactors relays operating safety controls and pan heaters
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 10 | ___ Drain and back flush cold-water sump and clean strainers
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 11 | ___ Clean inside of water tower using water hose scrape, brush and wipe as required
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 12 | ___ Check and clean spray nozzles
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 13 | ___ Inspect and clean float assembly bleed overflow and drain for proper operation
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 14 | ___ Inspect piping and valves for leaks tighten as required
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 15 | ___ Check damper motors and butterfly valves for proper operation Adjustment as required
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 16 | ___ Perform operational check adjust controls as required
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 17 | ___ Remove all debris from within and around unit
CT | UJPH-1005SA | CT - Cooling Tower - Semi-Annual | 18 | ___ Complete maintenance record and report deficiencies
DUST | UJPH-5090Q | Dust Collector - Quarterly | 1 | Monitor operation of collector for unusual noises, leaks and damage
DUST | UJPH-5090Q | Dust Collector - Quarterly | 2 | Shut off and bleed compressed air
DUST | UJPH-5090Q | Dust Collector - Quarterly | 3 | LOTO all power and compressed air
DUST | UJPH-5090Q | Dust Collector - Quarterly | 4 | Empty dust collection container
DUST | UJPH-5090Q | Dust Collector - Quarterly | 5 | Clean Interior and exterior of unit
DUST | UJPH-5090Q | Dust Collector - Quarterly | 6 | Clean and inspect all solenoids, valves and control devices; replace or repair as needed
DUST | UJPH-5090Q | Dust Collector - Quarterly | 7 | Inspect all wiring and connections for burns, damage and shorting; replace or repair as needed
DUST | UJPH-5090Q | Dust Collector - Quarterly | 8 | Clean and inspect all compressed air connections for leaks; replace or repair as needed
DUST | UJPH-5090Q | Dust Collector - Quarterly | 9 | Clean and inspect all doors, hardware and gaskets; replace or repair as needed
DUST | UJPH-5090Q | Dust Collector - Quarterly | 10 | Clean and inspect all ducts for leaks and missing caulking-seals; repair as needed
DUST | UJPH-5090Q | Dust Collector - Quarterly | 11 | Clean and inspect blower for proper clearance; replace or repair as needed
DUST | UJPH-5090Q | Dust Collector - Quarterly | 12 | Clean and inspect blower motor; oil as required by manufacture of motor
DUST | UJPH-5090Q | Dust Collector - Quarterly | 13 | Clean and inspect bearings and gear assemblies; grease or oil as required
DUST | UJPH-5090Q | Dust Collector - Quarterly | 14 | Clean and inspect hopper view ports
DUST | UJPH-5090Q | Dust Collector - Quarterly | 15 | Clean and inspect slide gate
DUST | UJPH-5090Q | Dust Collector - Quarterly | 16 | Inspect all brackets, mounting hardware and supports for loose bolts and corrosion
DUST | UJPH-5090Q | Dust Collector - Quarterly | 17 | Clean or replace filters as needed
DUST | UJPH-5090Q | Dust Collector - Quarterly | 18 | Clean or replace bags, cartridges as needed
DUST | UJPH-5090Q | Dust Collector - Quarterly | 19 | Drain moisture from compressor
DUST | UJPH-5090Q | Dust Collector - Quarterly | 20 | Remove LOTO, restore power and restart compressor
DUST | UJPH-5090Q | Dust Collector - Quarterly | 21 | Adjust pressures and controls to normal operation
EDISC | UJPH-1176A-IR | EDISC - Electrical Disconnect - Annual (IR) | 1 | SAFE WORK PRACTICES
EDISC | UJPH-1176A-IR | EDISC - Electrical Disconnect - Annual (IR) | 2 | ___ Visually inspect cover and cabinet for damage, holes or missing blank plates
EDISC | UJPH-1176A-IR | EDISC - Electrical Disconnect - Annual (IR) | 3 | ___ Remove panel covers and prepare to scan for any ?hot spots? or wiring deficiency?
EDISC | UJPH-1176A-IR | EDISC - Electrical Disconnect - Annual (IR) | 4 | ___ Visually inspect exposed sections of cables for physical damage and evidence of overheating
EDISC | UJPH-1176A-IR | EDISC - Electrical Disconnect - Annual (IR) | 5 | ___ Visually inspect wires, connections and cabinet for smoke - heat damage
EDISC | UJPH-1176A-IR | EDISC - Electrical Disconnect - Annual (IR) | 6 | ___ Inspect bolted electrical connections for high resistance using a thermo-graphic survey
EDISC | UJPH-1176A-IR | EDISC - Electrical Disconnect - Annual (IR) | 7 | ___ Reinstall covers and?clean area
EDISC | UJPH-1176A-IR | EDISC - Electrical Disconnect - Annual (IR) | 8 | ___ Complete maintenance record and report deficiencies
EPB | UJPH-1226A-IR | EPB - Electrical Panel Board - Annual (IR) | 1 | SAFE WORK PRACTICES
EPB | UJPH-1226A-IR | EPB - Electrical Panel Board - Annual (IR) | 2 | ___ Visually inspect cover and cabinet for damage, holes or missing blank plates
EPB | UJPH-1226A-IR | EPB - Electrical Panel Board - Annual (IR) | 3 | ___ Remove panel covers and prepare to scan for any ?hot spots? or wiring deficiency?
EPB | UJPH-1226A-IR | EPB - Electrical Panel Board - Annual (IR) | 4 | ___ Visually inspect exposed sections of cables for physical damage and evidence of overheating
EPB | UJPH-1226A-IR | EPB - Electrical Panel Board - Annual (IR) | 5 | ___ Visually inspect wires, connections and cabinet for smoke - heat damage
EPB | UJPH-1226A-IR | EPB - Electrical Panel Board - Annual (IR) | 6 | ___ Inspect bolted electrical connections for high resistance using a thermo-graphic survey
EPB | UJPH-1226A-IR | EPB - Electrical Panel Board - Annual (IR) | 7 | ___ Reinstall covers and?clean area
EPB | UJPH-1226A-IR | EPB - Electrical Panel Board - Annual (IR) | 8 | ___ Complete maintenance record and report deficiencies
ERV | UJPH-5012A | ERV - Energy Recovery Ventilator - Annual | 1 | SAFE WORK PRACTICES
ERV | UJPH-5012A | ERV - Energy Recovery Ventilator - Annual | 2 | ___ Check operation of unit
ERV | UJPH-5012A | ERV - Energy Recovery Ventilator - Annual | 3 | ___ Remove the filters
ERV | UJPH-5012A | ERV - Energy Recovery Ventilator - Annual | 4 | ___ Vacuum the exposed faces of the energy exchange core with a soft brush attachment
ERV | UJPH-5012A | ERV - Energy Recovery Ventilator - Annual | 5 | ___ DO NOT WASH THE ENERGY EXCHANGE CORE
ERV | UJPH-5012A | ERV - Energy Recovery Ventilator - Annual | 6 | ___ Vacuum clean the blower wheels at the same time you clean the face of the energy exchange core
ERV | UJPH-5012A | ERV - Energy Recovery Ventilator - Annual | 7 | ___ Install new filters
ERV | UJPH-5012A | ERV - Energy Recovery Ventilator - Annual | 8 | ___ Vacuum out dust from the rest of the unit case
ERV | UJPH-5012A | ERV - Energy Recovery Ventilator - Annual | 9 | ___ Complete maintenance record and report deficiencies
ERV | UJPH-5012Q | ERV - Energy Recovery Ventilator - Quarterly | 1 | SAFE WORK PRACTICES
ERV | UJPH-5012Q | ERV - Energy Recovery Ventilator - Quarterly | 2 | ___ Check operation of unit
ERV | UJPH-5012Q | ERV - Energy Recovery Ventilator - Quarterly | 3 | ___ Remove the filters and clean them
ERV | UJPH-5012Q | ERV - Energy Recovery Ventilator - Quarterly | 4 | ___ Reinstall filters
ERV | UJPH-5012Q | ERV - Energy Recovery Ventilator - Quarterly | 5 | ___ Complete maintenance record and report deficiencies
ERV | UJPH-5012SA | ERV - Energy Recovery Ventilator - Semi-Annual | 1 | SAFE WORK PRACTICES
ERV | UJPH-5012SA | ERV - Energy Recovery Ventilator - Semi-Annual | 2 | ___ Check operation of unit
ERV | UJPH-5012SA | ERV - Energy Recovery Ventilator - Semi-Annual | 3 | ___ Remove the filters and clean them
ERV | UJPH-5012SA | ERV - Energy Recovery Ventilator - Semi-Annual | 4 | ___ Reinstall filters
ERV | UJPH-5012SA | ERV - Energy Recovery Ventilator - Semi-Annual | 5 | ___ Complete maintenance record and report deficiencies
ESB | UJPH-1227A-IR | ESB - Electrical Switch Board - Annual (IR) | 1 | SAFE WORK PRACTICES
ESB | UJPH-1227A-IR | ESB - Electrical Switch Board - Annual (IR) | 2 | ___ Visually inspect cover and cabinet for damage, holes or missing blank plates
ESB | UJPH-1227A-IR | ESB - Electrical Switch Board - Annual (IR) | 3 | ___ Remove panel covers and prepare to scan for any ?hot spots? or wiring deficiency?
ESB | UJPH-1227A-IR | ESB - Electrical Switch Board - Annual (IR) | 4 | ___ Visually inspect exposed sections of cables for physical damage and evidence of overheating
ESB | UJPH-1227A-IR | ESB - Electrical Switch Board - Annual (IR) | 5 | ___ Visually inspect wires, connections and cabinet for smoke - heat damage
ESB | UJPH-1227A-IR | ESB - Electrical Switch Board - Annual (IR) | 6 | ___ Inspect bolted electrical connections for high resistance using a thermo-graphic survey
ESB | UJPH-1227A-IR | ESB - Electrical Switch Board - Annual (IR) | 7 | ___ Reinstall covers and?clean area
ESB | UJPH-1227A-IR | ESB - Electrical Switch Board - Annual (IR) | 8 | ___ Complete maintenance record and report deficiencies
ESG | UJPH-1210A-IR | ESG - Electrical Switchgear - Annual (IR) | 1 | SAFE WORK PRACTICES
ESG | UJPH-1210A-IR | ESG - Electrical Switchgear - Annual (IR) | 2 | ___ Visually inspect cover and cabinet for damage, holes or missing blank plates
ESG | UJPH-1210A-IR | ESG - Electrical Switchgear - Annual (IR) | 3 | ___ Remove panel covers and prepare to scan for any ?hot spots? or wiring deficiency?
ESG | UJPH-1210A-IR | ESG - Electrical Switchgear - Annual (IR) | 4 | ___ Visually inspect exposed sections of cables for physical damage and evidence of overheating
ESG | UJPH-1210A-IR | ESG - Electrical Switchgear - Annual (IR) | 5 | ___ Visually inspect wires, connections and cabinet for smoke - heat damage
ESG | UJPH-1210A-IR | ESG - Electrical Switchgear - Annual (IR) | 6 | ___ Inspect bolted electrical connections for high resistance using a thermo-graphic survey
ESG | UJPH-1210A-IR | ESG - Electrical Switchgear - Annual (IR) | 7 | ___ Reinstall covers and?clean area
ESG | UJPH-1210A-IR | ESG - Electrical Switchgear - Annual (IR) | 8 | ___ Complete maintenance record and report deficiencies
EVAP | UJPH-5013A | EVAP - Evaporator - Annual | 1 | SAFE WORK PRACTICES
EVAP | UJPH-5013A | EVAP - Evaporator - Annual | 2 | ___ Check units operating condition
EVAP | UJPH-5013A | EVAP - Evaporator - Annual | 3 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
EVAP | UJPH-5013A | EVAP - Evaporator - Annual | 4 | ___ Clean evaporator coils; straighten fins on coils
EVAP | UJPH-5013A | EVAP - Evaporator - Annual | 5 | ___ Clean drip pan, blowers, fans, motors and drain piping
EVAP | UJPH-5013A | EVAP - Evaporator - Annual | 6 | ___ On direct expansion systems, check for frosting or icing of coil
EVAP | UJPH-5013A | EVAP - Evaporator - Annual | 7 | ___ Replace all disposable filters, clean reusable filters
EVAP | UJPH-5013A | EVAP - Evaporator - Annual | 8 | ___ Clean exterior of unit
EVAP | UJPH-5013A | EVAP - Evaporator - Annual | 9 | ___ Complete maintenance record and report deficiencies
EVAP | UJPH-5013SA | EVAP - Evaporator - Semi-Annual | 1 | SAFE WORK PRACTICES
EVAP | UJPH-5013SA | EVAP - Evaporator - Semi-Annual | 2 | ___ Check units operating condition
EVAP | UJPH-5013SA | EVAP - Evaporator - Semi-Annual | 3 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
EVAP | UJPH-5013SA | EVAP - Evaporator - Semi-Annual | 4 | ___ Clean evaporator coils; straighten fins on coils
EVAP | UJPH-5013SA | EVAP - Evaporator - Semi-Annual | 5 | ___ Clean drip pan, blowers, fans, motors and drain piping
EVAP | UJPH-5013SA | EVAP - Evaporator - Semi-Annual | 6 | ___ On direct expansion systems, check for frosting or icing of coil
EVAP | UJPH-5013SA | EVAP - Evaporator - Semi-Annual | 7 | ___ Replace all disposable filters, clean reusable filters
EVAP | UJPH-5013SA | EVAP - Evaporator - Semi-Annual | 8 | ___ Clean exterior of unit
EVAP | UJPH-5013SA | EVAP - Evaporator - Semi-Annual | 9 | ___ Complete maintenance record and report deficiencies
FAN | UJPH-1027Q | FAN - Fan (Direct or Belt Drive) - Quarterly | 1 | SAFE WORK PRACTICES
FAN | UJPH-1027Q | FAN - Fan (Direct or Belt Drive) - Quarterly | 2 | ___ Check units operating condition
FAN | UJPH-1027Q | FAN - Fan (Direct or Belt Drive) - Quarterly | 3 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
FAN | UJPH-1027Q | FAN - Fan (Direct or Belt Drive) - Quarterly | 4 | ___ Lubricate motor and shaft bearings, if applicable
FAN | UJPH-1027Q | FAN - Fan (Direct or Belt Drive) - Quarterly | 5 | ___ Clean and check fan for noise and vibrations
FAN | UJPH-1027Q | FAN - Fan (Direct or Belt Drive) - Quarterly | 6 | ___ Check for proper operation of automatic and manual controls
FAN | UJPH-1027Q | FAN - Fan (Direct or Belt Drive) - Quarterly | 7 | ___ Belt Drive - Inspect belt and sheave, replace if necessary; ensure proper tension-alignment
FAN | UJPH-1027Q | FAN - Fan (Direct or Belt Drive) - Quarterly | 8 | ___ Direct Drive - Check motor mounts and set screws
FAN | UJPH-1027Q | FAN - Fan (Direct or Belt Drive) - Quarterly | 9 | ___ Check isolation bases for free movement
FAN | UJPH-1027Q | FAN - Fan (Direct or Belt Drive) - Quarterly | 10 | ___ Check rubber isolators for deterioration
FAN | UJPH-1027Q | FAN - Fan (Direct or Belt Drive) - Quarterly | 11 | ___ Clean housing and surrounding area
FAN | UJPH-1027Q | FAN - Fan (Direct or Belt Drive) - Quarterly | 12 | ___ Secure fan housing and guards replace missing nuts, bolts and screws
FAN | UJPH-1027Q | FAN - Fan (Direct or Belt Drive) - Quarterly | 13 | ___ Complete maintenance record and report deficiencies
FCU | UJPH-1012A | FCU - Fan Coil Unit - Annual | 1 | SAFE WORK PRACTICES
FCU | UJPH-1012A | FCU - Fan Coil Unit - Annual | 2 | ___ Check units operating condition Check with area personnel for deficiencies
FCU | UJPH-1012A | FCU - Fan Coil Unit - Annual | 3 | ___ Remove panel and vacuum coil and interior of unit
FCU | UJPH-1012A | FCU - Fan Coil Unit - Annual | 4 | ___ Clean dust and dirt from all grills, coils, fans, motors, and unit interior
FCU | UJPH-1012A | FCU - Fan Coil Unit - Annual | 5 | ___ Check operation of fan motor speeds and controls
FCU | UJPH-1012A | FCU - Fan Coil Unit - Annual | 6 | ___ Check coil and operation of control valve and thermostat
FCU | UJPH-1012A | FCU - Fan Coil Unit - Annual | 7 | ___ Check and clean drain lines and drain pan
FCU | UJPH-1012A | FCU - Fan Coil Unit - Annual | 8 | ___ Lubricate fan and motor bearings per manufacturer's recommendations
FCU | UJPH-1012A | FCU - Fan Coil Unit - Annual | 9 | ___ Clean and check fan blades/blower wheel for proper balance
FCU | UJPH-1012A | FCU - Fan Coil Unit - Annual | 10 | ___ Clean strainers if applicable Check and exercise hand valves
FCU | UJPH-1012A | FCU - Fan Coil Unit - Annual | 11 | ___ Verify proper water flow through coil
FCU | UJPH-1012A | FCU - Fan Coil Unit - Annual | 12 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
FCU | UJPH-1012A | FCU - Fan Coil Unit - Annual | 13 | ___ Replace filter ensure panels are re-installed properly
FCU | UJPH-1012A | FCU - Fan Coil Unit - Annual | 14 | ___ Complete maintenance record and report deficiencies
FCU | UJPH-1012SA | FCU - Fan Coil Unit - Semi-Annual | 1 | SAFE WORK PRACTICES
FCU | UJPH-1012SA | FCU - Fan Coil Unit - Semi-Annual | 2 | ___ Check units operating condition Check with area personnel for deficiencies
FCU | UJPH-1012SA | FCU - Fan Coil Unit - Semi-Annual | 3 | ___ Remove panel and vacuum coil and interior of unit
FCU | UJPH-1012SA | FCU - Fan Coil Unit - Semi-Annual | 4 | ___ Check coil and operation of control valve and thermostat
FCU | UJPH-1012SA | FCU - Fan Coil Unit - Semi-Annual | 5 | ___ Check coil, piping and control valve for leaks, damage and corrosion
FCU | UJPH-1012SA | FCU - Fan Coil Unit - Semi-Annual | 6 | ___ Check and clean drain lines and drain pan
FCU | UJPH-1012SA | FCU - Fan Coil Unit - Semi-Annual | 7 | ___ Clean strainers if applicable Check and exercise hand valves
FCU | UJPH-1012SA | FCU - Fan Coil Unit - Semi-Annual | 8 | ___ Verify proper water flow through coil
FCU | UJPH-1012SA | FCU - Fan Coil Unit - Semi-Annual | 9 | ___ Replace filter ensure panels are re-installed properly
FCU | UJPH-1012SA | FCU - Fan Coil Unit - Semi-Annual | 10 | ___ Complete maintenance record and report deficiencies
FILTER | UJPH-5025Q | FILTER - Filter (Pneumatic-Liquid) - Quarterly | 1 | SAFE WORK PRACTICES
FILTER | UJPH-5025Q | FILTER - Filter (Pneumatic-Liquid) - Quarterly | 2 | ___ Secure isolation valves and remove covers (Outage may be required)
FILTER | UJPH-5025Q | FILTER - Filter (Pneumatic-Liquid) - Quarterly | 3 | ___ Clean or replace filter element(s)
FILTER | UJPH-5025Q | FILTER - Filter (Pneumatic-Liquid) - Quarterly | 4 | ___ Check/clean seals and replace covers and open isolation valves
FILTER | UJPH-5025Q | FILTER - Filter (Pneumatic-Liquid) - Quarterly | 5 | ___ Clean connections, covers and area
FILTER | UJPH-5025Q | FILTER - Filter (Pneumatic-Liquid) - Quarterly | 6 | ___ Check all connection, valves and seals for leaks; Repair as needed
FILTER | UJPH-5025Q | FILTER - Filter (Pneumatic-Liquid) - Quarterly | 7 | ___ Complete maintenance record and report deficiencies
FTH | UJPH-1094A | FTH - Fin Tube Heater - Annual | 1 | SAFE WORK PRACTICES
FTH | UJPH-1094A | FTH - Fin Tube Heater - Annual | 2 | ___ Clean inside unit, fins and cover/grill
FTH | UJPH-1094A | FTH - Fin Tube Heater - Annual | 3 | ___ Straighten fins
FTH | UJPH-1094A | FTH - Fin Tube Heater - Annual | 4 | ___ Test controls, if applicable
FTH | UJPH-1094A | FTH - Fin Tube Heater - Annual | 5 | ___ Clean connections, covers and area
FTH | UJPH-1094A | FTH - Fin Tube Heater - Annual | 6 | ___ Complete maintenance record and report deficiencies
FURN | UJPH-1112A | FURN - Furnace - Annual | 1 | SAFE WORK PRACTICES
FURN | UJPH-1112A | FURN - Furnace - Annual | 2 | ___ Tighten all belts, wire connections and setscrews
FURN | UJPH-1112A | FURN - Furnace - Annual | 3 | ___ Clean evaporator and condenser coils
FURN | UJPH-1112A | FURN - Furnace - Annual | 4 | ___ Lubricate motor and fan shaft bearings
FURN | UJPH-1112A | FURN - Furnace - Annual | 5 | ___ Visually inspect belts and sheaves for proper tension and alignment Adjust/replace as needed
FURN | UJPH-1112A | FURN - Furnace - Annual | 6 | ___ Replace disposable filters, clean reusable filters
FURN | UJPH-1112A | FURN - Furnace - Annual | 7 | ___ Clean drain pans and drain lines Inspect for leaks
FURN | UJPH-1112A | FURN - Furnace - Annual | 8 | ___ Inspect all electrical terminals, connections and contactors Repair as needed
FURN | UJPH-1112A | FURN - Furnace - Annual | 9 | ___ Check power and control voltages
FURN | UJPH-1112A | FURN - Furnace - Annual | 10 | ___ Inspect motors for excessive noise and overheating, lube as required
FURN | UJPH-1112A | FURN - Furnace - Annual | 11 | ___ Check running amperage ____________
FURN | UJPH-1112A | FURN - Furnace - Annual | 12 | ___ Check all operating temperatures and pressures
FURN | UJPH-1112A | FURN - Furnace - Annual | 13 | ___ Check and adjust all temperature and pressure controls as needed
FURN | UJPH-1112A | FURN - Furnace - Annual | 14 | ___ Check and adjust all damper linkage as needed
FURN | UJPH-1112A | FURN - Furnace - Annual | 15 | ___ Check operation of all safeties
FURN | UJPH-1112A | FURN - Furnace - Annual | 16 | ___ Check flame signal
FURN | UJPH-1112A | FURN - Furnace - Annual | 17 | ___ Check burner wheel for dirt build-up and lint
FURN | UJPH-1112A | FURN - Furnace - Annual | 18 | ___ Check combustion intake louver and flue box for dirt buildup and wind born debris
FURN | UJPH-1112A | FURN - Furnace - Annual | 19 | ___ Inspect flue tubes and combustion chamber, cleaning as required
FURN | UJPH-1112A | FURN - Furnace - Annual | 20 | ___ Check all valves, piping and connections for leaks
FURN | UJPH-1112A | FURN - Furnace - Annual | 21 | ___ Remove burner gun assembly and inspect
FURN | UJPH-1112A | FURN - Furnace - Annual | 22 | ___ Clean the flame rod, ignition electrode, main burner disk and blast tube
FURN | UJPH-1112A | FURN - Furnace - Annual | 23 | ___ Check tightness of linkage fasteners and bolts, tighten as required
FURN | UJPH-1112A | FURN - Furnace - Annual | 24 | ___ Check quality of combustion test CO2 and CO look for irregularities in flame shape
FURN | UJPH-1112A | FURN - Furnace - Annual | 25 | ___ Ensure all guards, doors and access panels are secure no missing screws
FURN | UJPH-1112A | FURN - Furnace - Annual | 26 | ___ Clean connections, covers and area
FURN | UJPH-1112A | FURN - Furnace - Annual | 27 | ___ Complete maintenance record and report deficiencies
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 1 | SAFE WORK PRACTICES
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 2 | ___ Check units operating condition Check with area personnel for deficiencies
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 3 | ___ Inspect motors for excessive noise and overheating, lube as required
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 4 | ___ Visually inspect belts and sheaves for proper tension and alignment Adjust/replace if needed
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 5 | ___ Check all disposable filters, replace if needed, clean reusable filters
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 6 | ___ Clean drain pans and drain lines Inspect for leaks
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 7 | ___ Check power and control voltages
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 8 | ___ Record discharge temperature: ____________________
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 9 | ___ Check operation of all safeties
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 10 | ___ Check flame signal
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 11 | ___ Check burner wheel for dirt build-up and lint
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 12 | ___ Check combustion intake louver and flue box for dirt buildup and wind born debris
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 13 | ___ Inspect flue tubes and combustion chamber, cleaning as required
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 14 | ___ Check all valves, piping and connections for leaks
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 15 | ___ Ensure all guards, doors and access panels are secure, no missing screws
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 16 | ___ Clean connections, covers and area
FURN | UJPH-1112Q | FURN - Furnace - Quarterly | 17 | ___ Complete maintenance record and report deficiencies
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 1 | SAFE WORK PRACTICES
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 2 | ___ Record running time: beginning _______ hours ending _______ hours
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 3 | ___ FUEL - Check main supply tank level _______________
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 4 | ___ FUEL - Visually inspect and check day tank level _______________
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 5 | ___ FUEL - Visually inspect and test day tank float switch
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 6 | ___ FUEL - Visually inspect and test Supply or transfer pump operation
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 7 | ___ FUEL - Visually inspect and test Solenoid valve operation
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 8 | ___ FUEL - Check for water in system
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 9 | ___ FUEL - Visually inspect flexible hoses and connectors replace if necessary
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 10 | ___ FUEL - Clean strainer, filter, dirt leg or combination
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 11 | ___ FUEL - Check and test to see if tank vents and overflow piping are unobstructed
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 12 | ___ FUEL - Visually inspect piping
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 13 | ___ FUEL - Refill fuel in main tank if needed (IDIQ) or notify Government
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 14 | ___ LUBRICATION - Visually inspect and check oil level
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 15 | ___ LUBRICATION - Check lube oil heater
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 16 | ___ LUBRICATION - Visually inspect and clean or replace crankcase breather
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 17 | ___ LUBRICATION - Replace oil (every 50 run hours or annually)
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 18 | ___ LUBRICATION - Replace oil filter (every 50 run hours or annually)
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 19 | ___ COOLING - Visually inspect and check coolant level
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 20 | ___ COOLING - Check adequate cooling water to heat exchanger
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 21 | ___ COOLING - Check adequate fresh air through radiator
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 22 | ___ COOLING - Visually inspect water pump(s)
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 23 | ___ COOLING - Visually inspect and check condition of flexible hoses and connections
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 24 | ___ COOLING - Check jacket water heater
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 25 | ___ COOLING - Visually inspect and check fan and alternator belt
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 26 | ___ COOLING - Test antifreeze protection level
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 27 | ___ COOLING - Replace antifreeze if needed
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 28 | ___ COOLING - Clean rod out heat exchanger
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 29 | ___ COOLING - Clean exterior of radiator
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 30 | ___ COOLING - Visually inspect, check and clean ductwork and louvers
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 31 | ___ COOLING - Visually inspect, test and clean louver motor and controls
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 32 | ___ EXHAUST - Visually inspect and check for leakage
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 33 | ___ EXHAUST - Check and drain condensate trap
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 34 | ___ EXHAUST - Visually inspect insulation and fire hazards
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 35 | ___ EXHAUST - Visually inspect flexible exhaust sections
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 36 | ___ EXHAUST - Test for excessive back pressure
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 37 | ___ EXHAUST - Visually inspect exhaust system hangers and supports
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 38 | ___ BATTERY - Check electrolyte level
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 39 | ___ BATTERY - Visually inspect for corrosion remove, clean and dry if needed
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 40 | ___ BATTERY - Test specific gravity or state of charge
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 41 | ___ BATTERY - Visually inspect charger and charge rate
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 42 | ___ BATTERY - Check equalize charge
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 43 | ___ BATTERY - Visually inspect and check if terminals are clean and tight
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 44 | ___ ELECTRICAL - General visual inspection
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 45 | ___ ELECTRICAL - Visually inspect, check, clean and test circuit breakers and fuses
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 46 | ___ ELECTRICAL - Visually inspect and check for wire chafing where subject to movement
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 47 | ___ ELECTRICAL - Check and test operation of safeties and alarms
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 48 | ___ ELECTRICAL - Clean boxes, panels and cabinets
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 49 | ___ ELECTRICAL - Check control and power wiring connections tighten if needed
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 50 | ___ ELECTRICAL - Visually inspect and clean transfer switch main contacts
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 51 | ___ ELECTRICAL - Check and test calibration of voltage sensing relays/devices
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 52 | ___ ELECTRICAL - Test wire insulation breakdown (every 5 years or 500 hours only)
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 53 | ___ PRIME MOVER - General visual inspection
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 54 | ___ PRIME MOVER - Visually inspect and check governor oil level and linkage
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 55 | ___ PRIME MOVER - Clean or replace service air cleaner
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 56 | ___ PRIME MOVER - Check choke setting and carburetor adjustment
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 57 | ___ PRIME MOVER - Replace governor oil
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 58 | ___ PRIME MOVER - Visually inspect, check, clean and test the ignition system
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 59 | ___ PRIME MOVER - Test injector pump and injector for flow rate pressure and/or spray pattern
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 60 | ___ PRIME MOVER - Test EPS at minimum of 30% nameplate rating (every 3 to 4 years only)
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 61 | ___ PRIME MOVER - Test valve clearances (every 3 years or 500 hours only)
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 62 | ___ PRIME MOVER - Test torque bolts (every 3 years or 500 hours only)
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 63 | ___ GENERATOR - Visually inspect, check and clean brush length, appearance, free to move
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 64 | ___ GENERATOR - Visually inspect and clean commutator and slip rings
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 65 | ___ GENERATOR - Visually inspect and clean rotor and starter
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 66 | ___ GENERATOR - Visually inspect bearings replace if necessary (SO or IDIQ)
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 67 | ___ GENERATOR - Check bearing grease replace if necessary
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 68 | ___ GENERATOR - Visually inspect, check and clean the exciter
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 69 | ___ GENERATOR - Visually inspect, check and clean the voltage regulator
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 70 | ___ GENERATOR - Test, measure and record resistance readings of windings
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 71 | ___ GENERAL - General visual condition of EPSS
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 72 | ___ GENERAL - Service room, housing or pad housekeeping remove trash and debris
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 73 | ___ WRAP UP - Restore system to automatic operating condition
GENERATOR | UJPH-1252A | GEN - Generator (NFPA-110) - Annual | 74 | ___ WRAP UP - Complete maintenance record and report
HP | UJPH-1059A | HP - Heat Pump - Annual | 1 | SAFE WORK PRACTICES
HP | UJPH-1059A | HP - Heat Pump - Annual | 2 | ___ Check units operating condition Check with area personnel for deficiencies
HP | UJPH-1059A | HP - Heat Pump - Annual | 3 | ___ Check for frosting or icing of coils
HP | UJPH-1059A | HP - Heat Pump - Annual | 4 | ___ Clean intake side of condenser coils, fans and intake screens& straighten fins
HP | UJPH-1059A | HP - Heat Pump - Annual | 5 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
HP | UJPH-1059A | HP - Heat Pump - Annual | 6 | ___ Inspect motors for excessive noise and overheating, lube as required
HP | UJPH-1059A | HP - Heat Pump - Annual | 7 | ___ Inspect fan blades for clearance, should move freely
HP | UJPH-1059A | HP - Heat Pump - Annual | 8 | ___ Replace belts ensure proper tension Inspect sheaves ensure proper alignment
HP | UJPH-1059A | HP - Heat Pump - Annual | 9 | ___ Inspect piping, compressor and valve for leaks tighten all loose connections
HP | UJPH-1059A | HP - Heat Pump - Annual | 10 | ___ Check and record refrigerant pressure: __________________________
HP | UJPH-1059A | HP - Heat Pump - Annual | 11 | ___ Check operation of reversing valve
HP | UJPH-1059A | HP - Heat Pump - Annual | 12 | ___ Check compressor oil level if applicable
HP | UJPH-1059A | HP - Heat Pump - Annual | 13 | ___ Verify condensate drain system is operable
HP | UJPH-1059A | HP - Heat Pump - Annual | 14 | ___ Check operation of dampers and damper motors, and lubricate as required
HP | UJPH-1059A | HP - Heat Pump - Annual | 15 | ___ Replace all disposable filters, clean reusable filters
HP | UJPH-1059A | HP - Heat Pump - Annual | 16 | ___ Clean loose dirt and debris from interior and exterior of unit
HP | UJPH-1059A | HP - Heat Pump - Annual | 17 | ___ Complete maintenance record and report deficiencies
HP | UJPH-1059Q | HP - Heat Pump - Quarterly | 1 | SAFE WORK PRACTICES
HP | UJPH-1059Q | HP - Heat Pump - Quarterly | 2 | ___ Check units operating condition Check with area personnel for deficiencies
HP | UJPH-1059Q | HP - Heat Pump - Quarterly | 3 | ___ Check for frosting or icing of coils
HP | UJPH-1059Q | HP - Heat Pump - Quarterly | 4 | ___ Clean intake side of condenser coils, fans and intake screens& straighten fins
HP | UJPH-1059Q | HP - Heat Pump - Quarterly | 5 | ___ Inspect motors for excessive noise and overheating, lube as required
HP | UJPH-1059Q | HP - Heat Pump - Quarterly | 6 | ___ Visually inspect belts and sheaves for proper tension and alignment Adjust/replace as needed
HP | UJPH-1059Q | HP - Heat Pump - Quarterly | 7 | ___ Inspect piping, compressor and valve for leaks tighten all loose connections as necessary
HP | UJPH-1059Q | HP - Heat Pump - Quarterly | 8 | ___ Check operation of reversing valve
HP | UJPH-1059Q | HP - Heat Pump - Quarterly | 9 | ___ Check compressor oil level if applicable
HP | UJPH-1059Q | HP - Heat Pump - Quarterly | 10 | ___ Verify condensate drain system is operable
HP | UJPH-1059Q | HP - Heat Pump - Quarterly | 11 | ___ Replace all disposable filters, clean reusable filters
HP | UJPH-1059Q | HP - Heat Pump - Quarterly | 12 | ___ Clean loose dirt and debris from interior and exterior of unit
HP | UJPH-1059Q | HP - Heat Pump - Quarterly | 13 | ___ Complete maintenance record and report deficiencies
HTEX | UGSA-HVAC-HXR-01-01Y | HTEX - Heat Exchanger Plate-Frame - Annual | 1 | ___ Check exposed bolt threads, upper guide bars, rollers in moveable end frame and connecting frame.
HTEX | UGSA-HVAC-HXR-01-01Y | HTEX - Heat Exchanger Plate-Frame - Annual | 2 | ___ Clean and coat with a light grease.
HTEX | UGSA-HVAC-HXR-01-01Y | HTEX - Heat Exchanger Plate-Frame - Annual | 3 | ___ Check unpainted carbon steel surfaces, clean and coat with light grease, SAE-30 oil or other rust inhibiting product
HTEX | UGSA-HVAC-HXR-01-01Y | HTEX - Heat Exchanger Plate-Frame - Annual | 4 | ___ Check pressure and temperature gauges
HTEX | UGSA-HVAC-HXR-01-01Y | HTEX - Heat Exchanger Plate-Frame - Annual | 5 | ___ Back flush unit and clean in place annually or any time pressure/temperature profile exceeds set limits
HTEX | UGSA-HVAC-HXR-01-01Y | HTEX - Heat Exchanger Plate-Frame - Annual | 6 | ___ Check unit for leaks
HTEX | UGSA-HVAC-HXR-01-01Y | HTEX - Heat Exchanger Plate-Frame - Annual | 7 | ___ Follow manufactures trouble shooting guide to locate defective plates
HTEX | UGSA-HVAC-HXR-01-01Y | HTEX - Heat Exchanger Plate-Frame - Annual | 8 | ___ Check overall external appearance and condition of unit
HTEX | UJPH-1072A | HTEX - Heat Exchanger - Annual | 1 | SAFE WORK PRACTICES
HTEX | UJPH-1072A | HTEX - Heat Exchanger - Annual | 2 | ___ Visually inspect for leaks Tighten connections
HTEX | UJPH-1072A | HTEX - Heat Exchanger - Annual | 3 | ___ Check temperature gauges for proper operating temperatures
HTEX | UJPH-1072A | HTEX - Heat Exchanger - Annual | 4 | ___ Check steam modulating valve and steam condensate trap for proper operating
HTEX | UJPH-1072A | HTEX - Heat Exchanger - Annual | 5 | ___ Inspect immediate piping, valves drains and header for leaks Tighten in applicable
HTEX | UJPH-1072A | HTEX - Heat Exchanger - Annual | 6 | ___ Exercise isolation valves
HTEX | UJPH-1072A | HTEX - Heat Exchanger - Annual | 7 | ___ Clean strainers
HTEX | UJPH-1072A | HTEX - Heat Exchanger - Annual | 8 | ___ Inspect piping and exchanger for damaged insulation
HTEX | UJPH-1072A | HTEX - Heat Exchanger - Annual | 9 | ___ Complete maintenance record and report deficiencies
HUMID | UJPH-1035A-E | HUMID - Humidifier (Electric) - Annual | 1 | ___ Check canister
HUMID | UJPH-1035A-E | HUMID - Humidifier (Electric) - Annual | 2 | ___ Check heating element, remove scale
HUMID | UJPH-1035A-E | HUMID - Humidifier (Electric) - Annual | 3 | ___ Check and exercise all valves, adjust packing as needed
HUMID | UJPH-1035A-E | HUMID - Humidifier (Electric) - Annual | 4 | ___ Replace humidity canister, if necessary
HUMID | UJPH-1035A-E | HUMID - Humidifier (Electric) - Annual | 5 | ___ Check water level controller. Adjust/replace as necessary
HUMID | UJPH-1035A-E | HUMID - Humidifier (Electric) - Annual | 6 | ___ Inspect electrical wiring and connections, repair as needed
HUMID | UJPH-1035A-E | HUMID - Humidifier (Electric) - Annual | 7 | ___ Inspect insulation, repair as needed
HUMID | UJPH-1035A-E | HUMID - Humidifier (Electric) - Annual | 8 | ___ Test operation of unit
HUMID | UJPH-1035A-E | HUMID - Humidifier (Electric) - Annual | 9 | ___ Complete maintenance record and report deficiencies
HWH | UJPH-1131A | HWH - Water Heater (Electric) - Annual | 1 | SAFE WORK PRACTICES
HWH | UJPH-1131A | HWH - Water Heater (Electric) - Annual | 2 | ___ Visually inspect for leaks Repair if needed
HWH | UJPH-1131A | HWH - Water Heater (Electric) - Annual | 3 | ___ Inspect anode rod
HWH | UJPH-1131A | HWH - Water Heater (Electric) - Annual | 4 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
HWH | UJPH-1131A | HWH - Water Heater (Electric) - Annual | 5 | ___ Visually inspect immediate piping and tank insulation for damage
HWH | UJPH-1131A | HWH - Water Heater (Electric) - Annual | 6 | ___ Visually check relief valve for corrosion and leaks
HWH | UJPH-1131A | HWH - Water Heater (Electric) - Annual | 7 | ___ Drain sediment from tank
HWH | UJPH-1131A | HWH - Water Heater (Electric) - Annual | 8 | ___ Check automatic controls adjust temperature if needed
HWH | UJPH-1131A | HWH - Water Heater (Electric) - Annual | 9 | ___ Complete maintenance record and report deficiencies
HWH | UJPH-1133A | HWH - Water Heater (Gas) - Annual | 1 | SAFE WORK PRACTICES
HWH | UJPH-1133A | HWH - Water Heater (Gas) - Annual | 2 | ___ Visually inspect for leaks Repair if needed
HWH | UJPH-1133A | HWH - Water Heater (Gas) - Annual | 3 | ___ Check for gas leaks
HWH | UJPH-1133A | HWH - Water Heater (Gas) - Annual | 4 | ___ Check gas burner and pilot for proper flame adjust if required
HWH | UJPH-1133A | HWH - Water Heater (Gas) - Annual | 5 | ___ Check draft diverter and clear openings, if clogged
HWH | UJPH-1133A | HWH - Water Heater (Gas) - Annual | 6 | ___ Check condition of flue pipe, and chimney
HWH | UJPH-1133A | HWH - Water Heater (Gas) - Annual | 7 | ___ Exercise gas isolation valve
HWH | UJPH-1133A | HWH - Water Heater (Gas) - Annual | 8 | ___ Inspect anode rod
HWH | UJPH-1133A | HWH - Water Heater (Gas) - Annual | 9 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
HWH | UJPH-1133A | HWH - Water Heater (Gas) - Annual | 10 | ___ Visually inspect immediate piping and tank insulation for damage
HWH | UJPH-1133A | HWH - Water Heater (Gas) - Annual | 11 | ___ Visually check relief valve for corrosion and leaks
HWH | UJPH-1133A | HWH - Water Heater (Gas) - Annual | 12 | ___ Drain sediment from tank
HWH | UJPH-1133A | HWH - Water Heater (Gas) - Annual | 13 | ___ Check automatic controls adjust temperature if needed
HWH | UJPH-1133A | HWH - Water Heater (Gas) - Annual | 14 | ___ Complete maintenance record and report deficiencies
HWH | UJPH-1133Q | HWH - Water Heater (Gas) - Quarterly | 1 | SAFE WORK PRACTICES
HWH | UJPH-1133Q | HWH - Water Heater (Gas) - Quarterly | 2 | ___ Visually inspect for leaks Repair if needed
HWH | UJPH-1133Q | HWH - Water Heater (Gas) - Quarterly | 3 | ___ Check burner and pilot for proper flame
HWH | UJPH-1133Q | HWH - Water Heater (Gas) - Quarterly | 4 | ___ Check combustion exhaust system
HWH | UJPH-1133Q | HWH - Water Heater (Gas) - Quarterly | 5 | ___ Visually check relief valve for corrosion and leaks
HWH | UJPH-1133Q | HWH - Water Heater (Gas) - Quarterly | 6 | ___ Drain sediment from tank
HWH | UJPH-1133Q | HWH - Water Heater (Gas) - Quarterly | 7 | ___ Check automatic controls adjust temperature if needed
HWH | UJPH-1133Q | HWH - Water Heater (Gas) - Quarterly | 8 | ___ Complete maintenance record and report deficiencies
MCC | UJPH-1282A-IR | EMCC - Electrical Motor Control Center - Annual (IR) | 1 | SAFE WORK PRACTICES
MCC | UJPH-1282A-IR | EMCC - Electrical Motor Control Center - Annual (IR) | 2 | ___ Record operating conditions and settings
MCC | UJPH-1282A-IR | EMCC - Electrical Motor Control Center - Annual (IR) | 3 | ___ Check indicator lights, replace if required
MCC | UJPH-1282A-IR | EMCC - Electrical Motor Control Center - Annual (IR) | 4 | ___ Check for excessive heat, odors, noise, and vibrations
MCC | UJPH-1282A-IR | EMCC - Electrical Motor Control Center - Annual (IR) | 5 | ___ Inspect wiring, wiring connections and fuse blocks for charring, evidence of shorting
MCC | UJPH-1282A-IR | EMCC - Electrical Motor Control Center - Annual (IR) | 6 | ___ Inspect bolted electrical connections for high resistance using a thermo-graphic survey
MCC | UJPH-1282A-IR | EMCC - Electrical Motor Control Center - Annual (IR) | 7 | ___ Clean motor control center exterior and surrounding area
MCC | UJPH-1282A-IR | EMCC - Electrical Motor Control Center - Annual (IR) | 8 | ___ Complete maintenance record and report deficiencies
POWER | UJPH-5026A | POWER - Power Supply - Annual | 1 | SAFE WORK PRACTICES
POWER | UJPH-5026A | POWER - Power Supply - Annual | 2 | ___ Verify line voltages are within range
POWER | UJPH-5026A | POWER - Power Supply - Annual | 3 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring. Repair as required
POWER | UJPH-5026A | POWER - Power Supply - Annual | 4 | ___ Check for discolorations, hot spots, odors and charred insulation
POWER | UJPH-5026A | POWER - Power Supply - Annual | 5 | ___ Clean dirt from area
POWER | UJPH-5026A | POWER - Power Supply - Annual | 6 | ___ Complete maintenance record and report deficiencies
PUMP | UJPH-1049A | PUMP - Pump - Annual | 1 | SAFE WORK PRACTICES
PUMP | UJPH-1049A | PUMP - Pump - Annual | 2 | ___ Check for proper operation of pump
PUMP | UJPH-1049A | PUMP - Pump - Annual | 3 | ___ Exercise hand valve operation
PUMP | UJPH-1049A | PUMP - Pump - Annual | 4 | ___ Check for leaks on suction and discharge piping, seals, packing glands, etc
PUMP | UJPH-1049A | PUMP - Pump - Annual | 5 | ___ Check pump and motor operation for vibration, noise, overheating, etc
PUMP | UJPH-1049A | PUMP - Pump - Annual | 6 | ___ Inspect electrical connections and terminal for tightness and frayed wiring repair as needed
PUMP | UJPH-1049A | PUMP - Pump - Annual | 7 | ___ Check and clean strainers, if applicable
PUMP | UJPH-1049A | PUMP - Pump - Annual | 8 | ___ Inspect coolant circulation tubing for damage, crushing and flow
PUMP | UJPH-1049A | PUMP - Pump - Annual | 9 | ___ Visually inspect alignment of pump & motor
PUMP | UJPH-1049A | PUMP - Pump - Annual | 10 | ___ Inspect lovejoy coupling for damage, replace if necessary
PUMP | UJPH-1049A | PUMP - Pump - Annual | 11 | ___ Lubricate motor check oil level in reservoir if applicable
PUMP | UJPH-1049A | PUMP - Pump - Annual | 12 | ___ Lubricate pump if applicable
PUMP | UJPH-1049A | PUMP - Pump - Annual | 13 | ___ Inspect gauges and insulation
PUMP | UJPH-1049A | PUMP - Pump - Annual | 14 | ___ Tighten all nuts and bolts Inspect motor mounts and vibration pads
PUMP | UJPH-1049A | PUMP - Pump - Annual | 15 | ___ Clean exterior of pump, motor and immediate area
PUMP | UJPH-1049A | PUMP - Pump - Annual | 16 | ___ Complete maintenance record and report deficiencies
PUMP | UJPH-1049Q | PUMP - Pump - Quarterly | 1 | SAFE WORK PRACTICES
PUMP | UJPH-1049Q | PUMP - Pump - Quarterly | 2 | ___ Check for proper operation of pump
PUMP | UJPH-1049Q | PUMP - Pump - Quarterly | 3 | ___ Check for leaks on suction and discharge piping, seals, packing glands, etc
PUMP | UJPH-1049Q | PUMP - Pump - Quarterly | 4 | ___ Check pump and motor operation for vibration, noise, overheating, etc
PUMP | UJPH-1049Q | PUMP - Pump - Quarterly | 5 | ___ Check and clean strainers, if applicable
PUMP | UJPH-1049Q | PUMP - Pump - Quarterly | 6 | ___ Inspect coolant circulation tubing for damage, crushing and flow
PUMP | UJPH-1049Q | PUMP - Pump - Quarterly | 7 | ___ Inspect lovejoy coupling for damage, replace if necessary
PUMP | UJPH-1049Q | PUMP - Pump - Quarterly | 8 | ___ Complete maintenance record and report deficiencies
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 1 | SAFE WORK PRACTICES
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 2 | NOTE: Check RTU for bee?s and other animal nests
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 3 | ___ Replace all disposable filters, clean reusable filters
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 4 | ___ Replace belts ensure proper tension Inspect sheaves ensure proper alignment
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 5 | ___ Visually check coils and piping for leaks
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 6 | ___ Verify condensate drain system is operable
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 7 | ___ Inspect motors for excessive noise and overheating, lube as required
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 8 | ___ Inspect all electrical terminals, connections and contactors Repair as needed
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 9 | ___ Clean fan assembly Inspect fan and shaft for proper alignment Lubricate bearing as required
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 10 | ___ Clean all coils straighten fins as required
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 11 | ___ Inspect coil piping and valves for leaks tighten all connections as required
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 12 | ___ Check for proper water flow, temperature, and pressures through the coil
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 13 | ___ Check dampers and damper motors for proper operation adjust and lubricate as required
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 14 | ___ Inspect and confirm freeze protection systems
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 15 | ___ Clean loose dirt and debris from interior and exterior of unit
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 16 | ___ Inspect unit and note all corrosion of pan and RTU panels
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 17 | ___ Inspect area below RTU for water leaks
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 18 | ___ Clean interior and external surfaces of the plenum chamber including dampers and louvers
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 19 | ___ Check for damage to tie wires, binding bands, loose or broken connections, brackets and hangers
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 20 | ___ Verify all lights are working properly, replace bulbs as necessary
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 21 | ___ Verify all covers and guards are secured No missing fasteners
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 22 | ___ Check for improper level of equipment, defective sound isolators and vibration absorbers
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 23 | ___ Visually check RTU for proper operation & discharge temperatures
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 24 | ___ Record Temps: Discharge: _______________ Return: ________________________
RTU | UJPH-1239A | RTU - Rooftop Unit - Annual | 25 | ___ Complete maintenance record and report deficiencies
RTU | UJPH-1239Q | RTU - Rooftop Unit - Quarterly | 1 | SAFE WORK PRACTICES
RTU | UJPH-1239Q | RTU - Rooftop Unit - Quarterly | 2 | NOTE: Check RTU for bee?s and other animal nests
RTU | UJPH-1239Q | RTU - Rooftop Unit - Quarterly | 3 | ___ Visually check RTU for proper operation & discharge temperatures
RTU | UJPH-1239Q | RTU - Rooftop Unit - Quarterly | 4 | ___ Record Temps: Discharge: _______________ Return: ________________________
RTU | UJPH-1239Q | RTU - Rooftop Unit - Quarterly | 5 | ___ Visually inspect filters rotate roll filters if applicable Change filters if necessary
RTU | UJPH-1239Q | RTU - Rooftop Unit - Quarterly | 6 | ___ Visually check coils and piping for leaks
RTU | UJPH-1239Q | RTU - Rooftop Unit - Quarterly | 7 | ___ Verify condensate drain system is operable
RTU | UJPH-1239Q | RTU - Rooftop Unit - Quarterly | 8 | ___ Inspect and confirm freeze protection systems during from Nov to Apr
RTU | UJPH-1239Q | RTU - Rooftop Unit - Quarterly | 9 | ___ Inspect motors for excessive noise and overheating, lube as required
RTU | UJPH-1239Q | RTU - Rooftop Unit - Quarterly | 10 | ___ Verify all lights are working properly, replace bulbs
RTU | UJPH-1239Q | RTU - Rooftop Unit - Quarterly | 11 | ___ Verify all covers and guards are secured No missing fasteners
RTU | UJPH-1239Q | RTU - Rooftop Unit - Quarterly | 12 | ___ Complete maintenance record and report deficiencies
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 1 | SAFE WORK PRACTICES
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 2 | NOTE: Check RTU for bee?s and other animal nests
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 3 | ___ Replace all disposable filters, clean reusable filters
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 4 | ___ Visually check coils and piping for leaks
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 5 | ___ Verify condensate drain system is operable
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 6 | ___ Inspect motors for excessive noise and overheating, lube as required
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 7 | ___ Inspect all electrical terminals, connections and contactors Repair as needed
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 8 | ___ Clean fan assembly Inspect fan and shaft for proper alignment Lubricate bearing as required
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 9 | ___ Inspect coil piping and valves for leaks tighten all connections as required
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 10 | ___ Check dampers and damper motors for proper operation adjust and lubricate as required
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 11 | ___ Inspect and confirm freeze protection systems
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 12 | ___ Verify all lights are working properly, replace bulbs or repair as necessary
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 13 | ___ Verify all covers and guards are secured No missing fasteners
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 14 | ___ Visually check RTU for proper operation & discharge temperatures
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 15 | ___ Record Temps: Discharge: _______________ Return: ________________________
RTU | UJPH-1239SA | RTU - Rooftop Unit - Semi-Annual | 16 | ___ Complete maintenance record and report deficiencies
TANK | UJPH-1073A | TANK - Tank (Flash, Expansion, Condensate) - Annual | 1 | SAFE WORK PRACTICES
TANK | UJPH-1073A | TANK - Tank (Flash, Expansion, Condensate) - Annual | 2 | ___ Inspect exterior of tank and supports for damage, leaks and corrosion
TANK | UJPH-1073A | TANK - Tank (Flash, Expansion, Condensate) - Annual | 3 | ___ Inspect valves, pipes, fittings, drains and controls for leaks or damage
TANK | UJPH-1073A | TANK - Tank (Flash, Expansion, Condensate) - Annual | 4 | ___ Isolate and flush sediment from tank, if applicable (Water Only)
TANK | UJPH-1073A | TANK - Tank (Flash, Expansion, Condensate) - Annual | 5 | ___ Inspect associated insulation for damage
TANK | UJPH-1073A | TANK - Tank (Flash, Expansion, Condensate) - Annual | 6 | ___ Inspect relief valve, if applicable
TANK | UJPH-1073A | TANK - Tank (Flash, Expansion, Condensate) - Annual | 7 | ___ Clean immediate area around tank
TANK | UJPH-1073A | TANK - Tank (Flash, Expansion, Condensate) - Annual | 8 | ___ Complete maintenance record and report deficiencies
TANK | UJPH-1077A | TANK - Exterior Storage Tank - Annual | 1 | SAFE WORK PRACTICES
TANK | UJPH-1077A | TANK - Exterior Storage Tank - Annual | 2 | ___ Inspect exterior of tank and supports for damage, leaks and corrosion
TANK | UJPH-1077A | TANK - Exterior Storage Tank - Annual | 3 | ___ Inspect condition of roof hatches, if applicable Clean debris off top of tank
TANK | UJPH-1077A | TANK - Exterior Storage Tank - Annual | 4 | ___ Inspect condition of ladders, if applicable
TANK | UJPH-1077A | TANK - Exterior Storage Tank - Annual | 5 | ___ Inspect valves, pipes, fittings, drains and controls for leaks or damage
TANK | UJPH-1077A | TANK - Exterior Storage Tank - Annual | 6 | ___ Isolate and flush sediment from tank, if applicable (Water Only)
TANK | UJPH-1077A | TANK - Exterior Storage Tank - Annual | 7 | ___ Check for deterioration of tank foundation
TANK | UJPH-1077A | TANK - Exterior Storage Tank - Annual | 8 | ___ Inspect lighting system, if applicable
TANK | UJPH-1077A | TANK - Exterior Storage Tank - Annual | 9 | ___ Inspect associated insulation for damage
TANK | UJPH-1077A | TANK - Exterior Storage Tank - Annual | 10 | ___ Inspect relief valve, if applicable
TANK | UJPH-1077A | TANK - Exterior Storage Tank - Annual | 11 | ___ Clean immediate area around tank, remove all debris from containment area
TANK | UJPH-1077A | TANK - Exterior Storage Tank - Annual | 12 | ___ Inspect secondary containment for damage
TANK | UJPH-1077A | TANK - Exterior Storage Tank - Annual | 13 | ___ Complete maintenance record and report deficiencies
TANK | UJPH-1077SA | TANK - Exterior Storage Tank - Semi-Annual | 1 | SAFE WORK PRACTICES
TANK | UJPH-1077SA | TANK - Exterior Storage Tank - Semi-Annual | 2 | ___ Inspect exterior of tank and supports for damage, leaks and corrosion
TANK | UJPH-1077SA | TANK - Exterior Storage Tank - Semi-Annual | 3 | ___ Inspect condition of roof hatches, if applicable Clean debris off top of tank
TANK | UJPH-1077SA | TANK - Exterior Storage Tank - Semi-Annual | 4 | ___ Inspect condition of ladders, if applicable
TANK | UJPH-1077SA | TANK - Exterior Storage Tank - Semi-Annual | 5 | ___ Inspect valves, pipes, fittings, drains and controls for leaks or damage
TANK | UJPH-1077SA | TANK - Exterior Storage Tank - Semi-Annual | 6 | ___ Isolate and flush sediment from tank, if applicable (Water Only)
TANK | UJPH-1077SA | TANK - Exterior Storage Tank - Semi-Annual | 7 | ___ Check for deterioration of tank foundation
TANK | UJPH-1077SA | TANK - Exterior Storage Tank - Semi-Annual | 8 | ___ Inspect lighting system, if applicable
TANK | UJPH-1077SA | TANK - Exterior Storage Tank - Semi-Annual | 9 | ___ Inspect associated insulation for damage
TANK | UJPH-1077SA | TANK - Exterior Storage Tank - Semi-Annual | 10 | ___ Inspect relief valve, if applicable
TANK | UJPH-1077SA | TANK - Exterior Storage Tank - Semi-Annual | 11 | ___ Clean immediate area around tank, remove all debris from containment area
TANK | UJPH-1077SA | TANK - Exterior Storage Tank - Semi-Annual | 12 | ___ Inspect secondary containment for damage
TANK | UJPH-1077SA | TANK - Exterior Storage Tank - Semi-Annual | 13 | ___ Complete maintenance record and report deficiencies
UH | UJPH-1135A | UH - Unit Heater, Cabinet (Steam / HW) - Annual | 1 | SAFE WORK PRACTICES
UH | UJPH-1135A | UH - Unit Heater, Cabinet (Steam / HW) - Annual | 2 | ___ Check units operating condition Check with area personnel for deficiencies
UH | UJPH-1135A | UH - Unit Heater, Cabinet (Steam / HW) - Annual | 3 | ___ Inspect, clean and adjust control valves
UH | UJPH-1135A | UH - Unit Heater, Cabinet (Steam / HW) - Annual | 4 | ___ Clean grills, coil, fan, and unit interior and exterior
UH | UJPH-1135A | UH - Unit Heater, Cabinet (Steam / HW) - Annual | 5 | ___ Clean strainers Check and exercise hand valves
UH | UJPH-1135A | UH - Unit Heater, Cabinet (Steam / HW) - Annual | 6 | ___ Verify proper flow through coil
UH | UJPH-1135A | UH - Unit Heater, Cabinet (Steam / HW) - Annual | 7 | ___ Lubricate fan and motor bearings, if required
UH | UJPH-1135A | UH - Unit Heater, Cabinet (Steam / HW) - Annual | 8 | ___ Check fan blades/blower wheel Should move freely
UH | UJPH-1135A | UH - Unit Heater, Cabinet (Steam / HW) - Annual | 9 | ___ Inspect coils, connections, trap and piping for leaks
UH | UJPH-1135A | UH - Unit Heater, Cabinet (Steam / HW) - Annual | 10 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
UH | UJPH-1135A | UH - Unit Heater, Cabinet (Steam / HW) - Annual | 11 | ___ Check operation of fan motor speeds and controls
UH | UJPH-1135A | UH - Unit Heater, Cabinet (Steam / HW) - Annual | 12 | ___ Complete maintenance record and report deficiencies
UH | UJPH-1135SA | UH - Unit Heater, Cabinet (Steam / HW) - Semi-Annual | 1 | SAFE WORK PRACTICES
UH | UJPH-1135SA | UH - Unit Heater, Cabinet (Steam / HW) - Semi-Annual | 2 | ___ Check units operating condition Check with area personnel for deficiencies
UH | UJPH-1135SA | UH - Unit Heater, Cabinet (Steam / HW) - Semi-Annual | 3 | ___ Inspect, clean and adjust control valves
UH | UJPH-1135SA | UH - Unit Heater, Cabinet (Steam / HW) - Semi-Annual | 4 | ___ Clean grills, coil, fan, and unit interior and exterior
UH | UJPH-1135SA | UH - Unit Heater, Cabinet (Steam / HW) - Semi-Annual | 5 | ___ Clean strainers
UH | UJPH-1135SA | UH - Unit Heater, Cabinet (Steam / HW) - Semi-Annual | 6 | ___ Verify proper flow through coil
UH | UJPH-1135SA | UH - Unit Heater, Cabinet (Steam / HW) - Semi-Annual | 7 | ___ Lubricate fan and motor bearings, if required
UH | UJPH-1135SA | UH - Unit Heater, Cabinet (Steam / HW) - Semi-Annual | 8 | ___ Check fan blades/blower wheel Should move freely
UH | UJPH-1135SA | UH - Unit Heater, Cabinet (Steam / HW) - Semi-Annual | 9 | ___ Inspect coils, connections, trap and piping for leaks
UH | UJPH-1135SA | UH - Unit Heater, Cabinet (Steam / HW) - Semi-Annual | 10 | ___ Check operation of fan motor speeds and controls
UH | UJPH-1135SA | UH - Unit Heater, Cabinet (Steam / HW) - Semi-Annual | 11 | ___ Complete maintenance record and report deficiencies
UH | UJPH-1140A | IRH - Infrared Heater - Annual | 1 | SAFE WORK PRACTICES
UH | UJPH-1140A | IRH - Infrared Heater - Annual | 2 | ___ Check units operating condition Check with area personnel for deficiencies
UH | UJPH-1140A | IRH - Infrared Heater - Annual | 3 | ___ Inspect fuel system for leaks around the unit
UH | UJPH-1140A | IRH - Infrared Heater - Annual | 4 | ___ Replace primary intake filter, if applicable
UH | UJPH-1140A | IRH - Infrared Heater - Annual | 5 | ___ Blow out burner
UH | UJPH-1140A | IRH - Infrared Heater - Annual | 6 | ___ Clean spark electrode and reset gap
UH | UJPH-1140A | IRH - Infrared Heater - Annual | 7 | ___ Clean pilot and thermo-sensor bulb
UH | UJPH-1140A | IRH - Infrared Heater - Annual | 8 | ___ Check alignment of thermo-sensor bulb
UH | UJPH-1140A | IRH - Infrared Heater - Annual | 9 | ___ Inspect all electrical terminals, connections and contactors Repair as needed
UH | UJPH-1140A | IRH - Infrared Heater - Annual | 10 | ___ Check and clean pilot sight glass
UH | UJPH-1140A | IRH - Infrared Heater - Annual | 11 | ___ Clean area around unit
UH | UJPH-1140A | IRH - Infrared Heater - Annual | 12 | ___ Complete maintenance record and report deficiencies
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 1 | SAFE WORK PRACTICES
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 2 | ___ Check units operating condition Check with area personnel for deficiencies
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 3 | ___ Inspect, clean and adjust control valves
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 4 | ___ Inspect, clean and adjust electrodes and nozzles on oil burners
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 5 | ___ Inspect, clean and adjust control valves and thermo-sensing bulbs on gas burners
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 6 | ___ Lubricate oil burner motor bearings if applicable
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 7 | ___ Inspect fuel system for leaks
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 8 | ___ Replace all disposable filters, clean reusable filters
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 9 | ___ Check for proper operation of burner primary controls check and adjust thermostat
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 10 | ___ Check blower and motor for vibration and noise
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 11 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 12 | ___ Clean firebox
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 13 | ___ Clean blower and air plenum
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 14 | ___ Check condition of flue pipe, damper and stack
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 15 | ___ Clean around unit
UH | UJPH-1233A | UH - Unit Heater (Gas/Oil) - Annual | 16 | ___ Complete maintenance record and report deficiencies
UH | UJPH-1233SA | UH - Unit Heater (Gas/Oil) - Semi Annual | 1 | SAFE WORK PRACTICES
UH | UJPH-1233SA | UH - Unit Heater (Gas/Oil) - Semi Annual | 2 | ___ Inspect electrodes and nozzles on oil burners
UH | UJPH-1233SA | UH - Unit Heater (Gas/Oil) - Semi Annual | 3 | ___ Inspect control valves and thermo-sensing bulbs on gas burners
UH | UJPH-1233SA | UH - Unit Heater (Gas/Oil) - Semi Annual | 4
UH | UJPH-1233SA | UH - Unit Heater (Gas/Oil) - Semi Annual | 5 | ___ Inspect fuel system for leaks
UH | UJPH-1233SA | UH - Unit Heater (Gas/Oil) - Semi Annual | 6 | ___ Check for proper operation of burner primary controls check and adjust thermostat
UH | UJPH-1233SA | UH - Unit Heater (Gas/Oil) - Semi Annual | 7 | ___ Check blower and motor for vibration and noise
UH | UJPH-1233SA | UH - Unit Heater (Gas/Oil) - Semi Annual | 8 | ___ Check condition of flue pipe, damper and stack
UH | UJPH-1233SA | UH - Unit Heater (Gas/Oil) - Semi Annual | 9 | ___ Clean around unit
UH | UJPH-1233SA | UH - Unit Heater (Gas/Oil) - Semi Annual | 10 | ___ Complete maintenance record and report deficiencies
UH | UJPH-1233SA | UH - Unit Heater (Gas/Oil) - Semi Annual | 11 | ___ Check units operating condition Check with area personnel for deficiencies
UH | UJPH-1233SA | UH - Unit Heater (Gas/Oil) - Semi Annual | 12 | ___ Inspect control valves
UH | UJPH-1234A | UH - Unit Heater (Electric) - Annual | 1 | SAFE WORK PRACTICES
UH | UJPH-1234A | UH - Unit Heater (Electric) - Annual | 2 | ___ Check units operating condition Check with area personnel for deficiencies
UH | UJPH-1234A | UH - Unit Heater (Electric) - Annual | 3 | ___ Clean grills, coil, fan, and unit interior and exterior
UH | UJPH-1234A | UH - Unit Heater (Electric) - Annual | 4 | ___ Lubricate fan and motor bearings, if required
UH | UJPH-1234A | UH - Unit Heater (Electric) - Annual | 5 | ___ Check fan blades/blower wheel Should move freely
UH | UJPH-1234A | UH - Unit Heater (Electric) - Annual | 6 | ___ Inspect all electrical connections and terminals for tightness and frayed wiring
UH | UJPH-1234A | UH - Unit Heater (Electric) - Annual | 7 | ___ Check operation of fan motor speeds and controls
UH | UJPH-1234A | UH - Unit Heater (Electric) - Annual | 8 | ___ Complete maintenance record and report deficiencies
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 1 | SAFE WORK PRACTICES
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 2 | NOTE: May require an OUTAGE to be scheduled
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 3 | Notify personnel and test UPS fault alarm system
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 4 | ___ Check with the operating or area personnel for any obvious deficiencies
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 5 | ___ Check electrolyte level of batteries; add water as required; check terminals for corrosion, clean as required
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 6 | ___ Check 25% of the batteries for charge and electrolyte specific gravity
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 7 | ___ Check batteries for cracks and leaks
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 8 | ___ Check 25% of the terminal-to-cell connection resistance; rehabilitate connections as required
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 9 | ___ Measure and record individual cell and string float voltages
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 10 | ___ Check integrity of battery rack
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 11 | ___ Check battery room temperature and ventilation system
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 12 | ___ Replace air filters on UPS modules
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 13 | ___ Check output voltage and amperages, from control panel
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 14 | ___ Check UPS room temperature and ventilation system
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 15 | ___ Notify personnel and test UPS fault alarm system
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 16 | ___ Clean around batteries and UPS modules
UPS | UJPH-2086A | UPS - Uninterrupted Power Supply (RS Means) - Annual | 17 | ___ Complete maintenance record and report deficiencies
UPS | UJPH-2086SA | UPS - Uninterrupted Power Supply (RS Means) - Semi-Annual | 1 | SAFE WORK PRACTICES
UPS | UJPH-2086SA | UPS - Uninterrupted Power Supply (RS Means) - Semi-Annual | 2 | NOTE: May require an OUTAGE to be scheduled
UPS | UJPH-2086SA | UPS - Uninterrupted Power Supply (RS Means) - Semi-Annual | 3 | Notify personnel and test UPS fault alarm system
UPS | UJPH-2086SA | UPS - Uninterrupted Power Supply (RS Means) - Semi-Annual | 4 | ___ Check with the operating or area personnel for any obvious deficiencies
UPS | UJPH-2086SA | UPS - Uninterrupted Power Supply (RS Means) - Semi-Annual | 5 | ___ Check 25% of the batteries for charge and electrolyte specific gravity
UPS | UJPH-2086SA | UPS - Uninterrupted Power Supply (RS Means) - Semi-Annual | 6 | ___ Check batteries for cracks and leaks
UPS | UJPH-2086SA | UPS - Uninterrupted Power Supply (RS Means) - Semi-Annual | 7 | ___ Check 25% of the terminal-to-cell connection resistance; rehabilitate connections as required
UPS | UJPH-2086SA | UPS - Uninterrupted Power Supply (RS Means) - Semi-Annual | 8 | ___ Check battery room temperature and ventilation system
UPS | UJPH-2086SA | UPS - Uninterrupted Power Supply (RS Means) - Semi-Annual | 9 | ___ Replace air filters on UPS modules
UPS | UJPH-2086SA | UPS - Uninterrupted Power Supply (RS Means) - Semi-Annual | 10 | ___ Check output voltage and amperages, from control panel
UPS | UJPH-2086SA | UPS - Uninterrupted Power Supply (RS Means) - Semi-Annual | 11 | ___ Check UPS room temperature and ventilation system
UPS | UJPH-2086SA | UPS - Uninterrupted Power Supply (RS Means) - Semi-Annual | 12 | ___ Notify personnel and test UPS fault alarm system
UPS | UJPH-2086SA | UPS - Uninterrupted Power Supply (RS Means) - Semi-Annual | 13 | ___ Clean around batteries and UPS modules
UPS | UJPH-2086SA | UPS - Uninterrupted Power Supply (RS Means) - Semi-Annual | 14 | ___ Complete maintenance record and report deficiencies
VAC | UGSA-HVAC-PMP-02-01Y | VAC - Vacuum Producer - Annual | 1 | ___ Drain oil from reservoir if applicable. Place oil in a proper receptacle for oil disposal.
VAC | UGSA-HVAC-PMP-02-01Y | VAC - Vacuum Producer - Annual | 2 | ___ Remove oil filter and replace, if applicable.
VAC | UGSA-HVAC-PMP-02-01Y | VAC - Vacuum Producer - Annual | 3 | ___ Remove oil sight glass and clean as needed.
VAC | UGSA-HVAC-PMP-02-01Y | VAC - Vacuum Producer - Annual | 4 | ___ Fill with the appropriate type and amount of oil if applicable. Refer to manufacturer?s specifications for the equipment.
VAC | UGSA-HVAC-PMP-02-01Y | VAC - Vacuum Producer - Annual | 5 | ___ Remove the exhaust filter and replace.
VAC | UGSA-HVAC-PMP-02-01Y | VAC - Vacuum Producer - Annual | 6 | ___ Check the exhaust chamber and oil return line for clogging. Clean if needed.
VAC | UGSA-HVAC-PMP-02-01Y | VAC - Vacuum Producer - Annual | 7 | ___ Inspect the exhaust chamber for excess oil. Wipe out if needed.
VAC | UGSA-HVAC-PMP-02-01Y | VAC - Vacuum Producer - Annual | 8 | ___ Inspect the vacuum inlet filter.
VAC | UGSA-HVAC-PMP-02-01Y | VAC - Vacuum Producer - Annual | 9 | ___ Wipe out the interior of the filter housing
VAC | UGSA-HVAC-PMP-02-01Y | VAC - Vacuum Producer - Annual | 10 | ___ Wipe exterior surfaces of the pump free of debris and oil.
VAC | UGSA-HVAC-PMP-02-01Y | VAC - Vacuum Producer - Annual | 11 | ___ Remove and clean the vacuum diverter valve. Replace with new if needed.
VAC | UGSA-HVAC-PMP-02-01Y | VAC - Vacuum Producer - Annual | 12 | ___ If applicable, check the drive belt for cracks fraying and stretching. Replace if worn
VAV | UJPH-1038A | VAV - Variable Air Volume Box - Annual | 1 | SAFE WORK PRACTICES
VAV | UJPH-1038A | VAV - Variable Air Volume Box - Annual | 2 | ___ Open / Close VAV control box
VAV | UJPH-1038A | VAV - Variable Air Volume Box - Annual | 3 | ___ Check that pneumatic tubing and/or electrical connections are in place and tight
VAV | UJPH-1038A | VAV - Variable Air Volume Box - Annual | 4 | ___ Inspect connecting ducts for leaks Correct all leaks as needed
VAV | UJPH-1038A | VAV - Variable Air Volume Box - Annual | 5 | ___ Check and clean reheat coil, if applicable
VAV | UJPH-1038A | VAV - Variable Air Volume Box - Annual | 6 | ___ Inspect damper activators for tightness to mounting brackets
VAV | UJPH-1038A | VAV - Variable Air Volume Box - Annual | 7 | ___ Tighten arm on motor output shaft
VAV | UJPH-1038A | VAV - Variable Air Volume Box - Annual | 8 | ___ Change filters if applicable
VAV | UJPH-1038A | VAV - Variable Air Volume Box - Annual | 9 | ___ FAN POWERED - Check fan operation, lubricate motor and shaft bearings as needed
VAV | UJPH-1038A | VAV - Variable Air Volume Box - Annual | 10 | ___ Lubricate actuator linkage and damper blade pivot points
VAV | UJPH-1038A | VAV - Variable Air Volume Box - Annual | 11 | ___ Cycle actuator while watching for proper operation Verify that blades fully open and close
VAV | UJPH-1038A | VAV - Variable Air Volume Box - Annual | 12 | ___ Complete maintenance record and report deficiencies
VFD | UJPH-1036A | VFD - Variable Frequency Drive - Annual | 1 | SAFE WORK PRACTICES
VFD | UJPH-1036A | VFD - Variable Frequency Drive - Annual | 2 | ___ Inspect operation of VFD
VFD | UJPH-1036A | VFD - Variable Frequency Drive - Annual | 3 | ___ Secure power to unit LOTO
VFD | UJPH-1036A | VFD - Variable Frequency Drive - Annual | 4 | ___ Inspect wiring and fuse blocks for looseness, charring, evidence of overheating
VFD | UJPH-1036A | VFD - Variable Frequency Drive - Annual | 5 | ___ Inspect fan for proper operation
VFD | UJPH-1036A | VFD - Variable Frequency Drive - Annual | 6 | ___ Clean interior and exterior of cabinet
VFD | UJPH-1036A | VFD - Variable Frequency Drive - Annual | 7 | ___ Restore power and bring unit back online
VFD | UJPH-1036A | VFD - Variable Frequency Drive - Annual | 8 | ___ Complete maintenance record and report deficiencies
XFMR | UJPH-1093A-D | XFMR - Electrical Transformer - Annual (Dry) | 1 | SAFE WORK PRACTICES
XFMR | UJPH-1093A-D | XFMR - Electrical Transformer - Annual (Dry) | 2 | ___ Examine the exterior of the transformer for any damage
XFMR | UJPH-1093A-D | XFMR - Electrical Transformer - Annual (Dry) | 3 | ___ Remove covers or open doors
XFMR | UJPH-1093A-D | XFMR - Electrical Transformer - Annual (Dry) | 4 | ___ Check for signs of moisture or overheating
XFMR | UJPH-1093A-D | XFMR - Electrical Transformer - Annual (Dry) | 5 | ___ Check for voltage creeping over insulated surfaces
XFMR | UJPH-1093A-D | XFMR - Electrical Transformer - Annual (Dry) | 6 | ___ Check fans, motors, and other auxiliary devices for proper operation where applicable
XFMR | UJPH-1093A-D | XFMR - Electrical Transformer - Annual (Dry) | 7 | ___ Check the condition of the ground system
XFMR | UJPH-1093A-D | XFMR - Electrical Transformer - Annual (Dry) | 8 | ___ Clean transformer exterior and surrounding area
XFMR | UJPH-1093A-D | XFMR - Electrical Transformer - Annual (Dry) | 9 | ___ Complete maintenance record and report deficiencies